## Equipment
Unit ID | Customer / building | Service address | Location on site | Type | Make | Outdoor model | Outdoor serial | Indoor unit (model / serial) | Installed | Refrigerant | Factory charge (lb) | Filter size(s) | Belt | Parts warranty ends | Agreement tier | Last serviced | Next due | Days to next due | Notes
AND-01 | Anderson, Mark | 412 Laurel Ridge Dr, Cary NC | Condenser side yard; furnace in attic | Split AC + gas furnace | Trane | 4TTR4036 | 24151ABCD | S9V2B060U4 / 2415M1234 | 2024-05-20 | R-410A | 7.4 | 20x25x1 | none | 2034-05-20 | Silver | 2026-04-14 | 2026-10-15 | 40 | Attic pull-down ladder in hall. Gate code 4471.
BAK-01 | Baker, Janet | 88 Millbrook Ln, Raleigh NC | Condenser rear; air handler garage closet | Heat pump + air handler | Goodman | GSZ140361 | 2312145678 | ARUF37C14 / 2312998877 | 2024-01-22 | R-410A | 6.9 | 16x25x1 | none | 2034-01-22 | Bronze | 2026-06-08 | 2027-01-08 | 125 | Small dog, friendly. Text before arriving.
CAS-01 | Castillo, Rosa | 1509 Pine Hollow Ct, Apex NC | Condenser left side; furnace crawlspace | Split AC + gas furnace | Carrier | 24ACC636A003 | 2419E12345 | 59SC2C080 / 2419A77665 | 2024-06-03 | R-410A | 8.1 | 20x20x4 | none | 2034-06-03 | Gold | 2026-04-21 | 2026-10-20 | 45 | Crawlspace access at rear. Media filter cabinet.
DAW-01 | Dawson, Phil | 27 Old Mill Rd, Garner NC | Condenser rear; air handler attic | Heat pump + air handler | Rheem | RP1436AJ1NA | W0125ABC | RH1T3617 / W0125XYZ | 2021-04-08 | R-410A | 6.5 | 16x20x1 | none | 2031-04-08 | Bronze | 2026-06-16 |  |  | Attic is tight; bring drop light.
ELL-01 | Ellis, Tanya | 3301 Falls Creek Way, Wake Forest NC | Condenser right side; furnace basement | Split AC + gas furnace | Lennox | ML14XC1-036 | 5824K00123 | ML180UH070 / 5824C00456 | 2024-09-12 | R-410A | 7 | 20x25x1 | none | 2034-09-12 | Silver | 2026-07-07 |  |  | Float switch on secondary drain pan.
GAR-01 | Garcia, Luis | 1180 Kildaire Farm Rd, Cary NC | Condenser rear; furnace attic | Split AC + gas furnace (variable speed) | Carrier | 24VNA936A003 | 1226E54321 | 59MN7A080 / 1226A11223 | 2023-03-14 | R-410A | 9.2 | 20x25x4 | none | 2033-03-14 | Gold | 2026-05-19 | 2026-11-03 | 59 | Infinity control. Homeowner wants readings emailed.
PAT-01 | Patel, Raj | 1601 Davis Dr, Morrisville NC | Unit 1: condenser left; furnace attic (upstairs zone) | Split AC + gas furnace | Trane | 4TTV8036 | 24374IJKL | S9V2C080 / 2437M5566 | 2024-09-20 | R-410A | 8.4 | 20x25x1 | none | 2034-09-20 | Gold | 2026-07-22 | 2027-01-20 | 137 | Two-system home; this row is the upstairs system.
PAT-02 | Patel, Raj | 1601 Davis Dr, Morrisville NC | Unit 2: condenser right; air handler closet (downstairs zone) | Split AC + gas furnace | Trane | 4TTV8024 | 24374MNOP | S9V2B040 / 2437M7788 | 2024-09-20 | R-410A | 6.6 | 16x20x1 | none | 2034-09-20 | Gold | 2026-07-22 | 2027-01-20 | 137 | Downstairs system, same agreement as PAT-01.
WAL-01 | Walsh, Tom | 9 Deer Track Ln, Apex NC | Condenser rear; air handler attic | Heat pump + air handler | Lennox | XP25-036 | 5824L00987 | CBA38MV-036 / 5824C09876 | 2024-10-01 | R-410A | 8 | 20x25x4 | none | 2034-10-01 | Gold | 2026-08-04 | 2026-11-12 | 68 | iComfort thermostat. Surge protector on disconnect.
YOU-01 | Young, Brenda | 1230 Buck Jones Rd, Raleigh NC | Condenser side; furnace garage | Split AC + gas furnace | Trane | 4TTR6036 | 23189QRST | S9X2B060 / 2318M4455 | 2023-05-30 | R-410A | 7.6 | 20x25x1 | none | 2033-05-30 | Silver | 2026-05-06 | 2026-11-06 | 62 | Garage code 2280. Filter behind louvered door.
NGU-01 | Nguyen, An | 302 Chapel Ridge Rd, Cary NC | Condenser rear; air handler attic | Heat pump + air handler | Lennox | ML17XP1-048 | 5825K00789 | CBA27UHE-048 / 2625C00321 | 2026-04-22 | R-454B | 8.9 | 20x25x4 | none | 2036-04-22 | Gold | 2026-04-22 | 2026-10-22 | 47 | A2L refrigerant: leak detection sensor in air handler. Registered 4/24/2026.
MBD-RTU1 | Millbrook Dental (Dr. Ortiz) | 2200 Millbrook Rd, Raleigh NC | Roof, NE corner, serves exam rooms | Package rooftop unit, 7.5 ton | Carrier | 48TCED08A2A5 | 3222C41198 | n/a (packaged) | 2022-08-15 | R-410A | 14.2 | 4x 20x20x2 | A-42 | 2027-08-15 | none | 2026-09-01 | 2026-12-01 | 87 | Commercial PM contract, quarterly. Roof hatch key in office. Economizer.
MBD-RTU2 | Millbrook Dental (Dr. Ortiz) | 2200 Millbrook Rd, Raleigh NC | Roof, SW corner, serves lobby and offices | Package rooftop unit, 5 ton | Carrier | 48TCEA06A2A5 | 3222C41205 | n/a (packaged) | 2022-08-15 | R-410A | 10.8 | 4x 16x20x2 | A-40 | 2027-08-15 | none | 2026-09-01 | 2026-12-01 | 87 | Same contract as RTU1. Belt spare kept in mechanical closet.
Formulas:
Last serviced = IF([Unit ID]="","",IF(MAXIFS('Service log'!$A:$A,'Service log'!$B:$B,[Unit ID])=0,"",MAXIFS('Service log'!$A:$A,'Service log'!$B:$B,[Unit ID])))
Next due = IF([Last serviced]="","",IF(MAXIFS('Service log'!$P:$P,'Service log'!$B:$B,[Unit ID])=0,"",MAXIFS('Service log'!$P:$P,'Service log'!$B:$B,[Unit ID])))
Days to next due = IF([Next due]="","",[Next due]-TODAY())

## Service log
Date | Unit ID | Customer | Model | Service type | Tech | Work done / findings | Readings | Parts replaced | Refrigerant added (lb) | Refrigerant type | Labor hours | Invoice total | Invoice / job # | Agreement visit? | Next due | Checklist / photos
2025-10-15 | AND-01 | Anderson, Mark | 4TTR4036 | Maintenance | Dave R. | Fall tune-up. Cleaned flame sensor, inspected heat exchanger with camera (no cracks), tested limit and rollout switches, cleared condensate trap, replaced filter. Homeowner shown rise reading. | Temp rise 46 F (rated 35-65); gas 3.5 in WC; TESP 0.58 in WC; blower 4.1 A; inducer 0.9 A; CO in flue 14 ppm | Filter 20x25x1 | 0 | R-410A | 1.25 | 0 | J-10422 | Yes | 2026-04-15 | usedeepsel.com/furnace-maintenance-checklist
2025-10-20 | CAS-01 | Castillo, Rosa | 24ACC636A003 | Maintenance | Dave R. | Fall tune-up. Burners cleaned, igniter checked (7 years old, reads 62 ohms, fine), venting checked, media filter changed. | Temp rise 52 F; gas 3.4 in WC; TESP 0.71 in WC (media filter); blower 5.0 A; CO 9 ppm | Media filter 20x20x4 | 0 | R-410A | 1.5 | 0 | J-10431 | Yes | 2026-04-20 | usedeepsel.com/furnace-maintenance-checklist
2025-11-03 | GAR-01 | Garcia, Luis | 24VNA936A003 | Repair | Mike T. | No-heat call. Hot surface igniter open circuit. Replaced, cycled 3 times, verified ignition. Gold discount 15% applied. | Igniter reads open; after repair rise 48 F; gas 3.5 in WC | Hot surface igniter | 0 | R-410A | 1.5 | 246.5 | J-10488 | No |  | photos: job J-10488
2025-11-12 | WAL-01 | Walsh, Tom | XP25-036 | Maintenance | Dave R. | Fall heat-pump check. Defrost cycle forced and timed, aux heat strips staged and amped, reversing valve verified, filter changed. | Heat mode: ΔT 24 F; strips 19.8 A per stage; defrost 6 min; outdoor coil clean | Media filter 20x25x4 | 0 | R-410A | 1.25 | 0 | J-10502 | Yes | 2026-05-12 | usedeepsel.com/heat-pump-maintenance-checklist
2025-12-02 | MBD-RTU1 | Millbrook Dental (Dr. Ortiz) | 48TCED08A2A5 | Inspection | Mike T. | Q4 quarterly per contract task list: belts, filters, condenser and evap coil, drain, economizer damper and linkage, electrical connections torqued, log left on unit. | Belt A-42 cracked, replaced; filters 4x 20x20x2 replaced; ΔT heat 34 F; supply fan 6.1 A; gas 3.5 in WC | Belt A-42; 4 filters 20x20x2 | 0 | R-410A | 2 | 0 | J-10560 | No | 2026-03-02 | usedeepsel.com/commercial-hvac-maintenance-checklist
2025-12-02 | MBD-RTU2 | Millbrook Dental (Dr. Ortiz) | 48TCEA06A2A5 | Inspection | Mike T. | Q4 quarterly. Same task list as RTU1. Economizer minimum position reset to 15%. | Belt A-40 ok; filters replaced; ΔT heat 33 F; fan 4.4 A | 4 filters 16x20x2 | 0 | R-410A | 1.5 | 0 | J-10560 | No | 2026-03-02 | usedeepsel.com/commercial-hvac-maintenance-checklist
2026-01-08 | BAK-01 | Baker, Janet | GSZ140361 | Maintenance | Dave R. | First agreement visit. Heat-pump winter check, strips verified, filter changed, thermostat schedule reviewed with homeowner. | Heat ΔT 22 F; strips 18.9 A; defrost normal; filter was 4 months old | Filter 16x25x1 | 0 | R-410A | 1 | 0 | J-10611 | Yes | 2026-06-08 | usedeepsel.com/heat-pump-maintenance-checklist
2026-02-11 | PAT-01 | Patel, Raj | 4TTV8036 | Warranty | Mike T. | Inducer motor bearing noise. Replaced under Trane 10-year parts warranty; labor billed. Serial and install date pulled from this sheet for the claim. | Inducer 1.6 A before (rated 1.1), 1.0 A after | Inducer motor (warranty part) | 0 | R-410A | 2 | 180 | J-10677 | No |  | claim ref TR-2026-0219
2026-03-02 | MBD-RTU1 | Millbrook Dental (Dr. Ortiz) | 48TCED08A2A5 | Inspection | Mike T. | Q1 quarterly. Coils rinsed, drain pan treated, contactor and capacitors checked, economizer verified on 55 F day. | Fan 6.0 A; cap 45/7.5 reads 44.2/7.3; contactor slight pitting, noted | none | 0 | R-410A | 1.75 | 0 | J-10740 | No | 2026-06-01 | usedeepsel.com/commercial-hvac-maintenance-checklist
2026-03-02 | MBD-RTU2 | Millbrook Dental (Dr. Ortiz) | 48TCEA06A2A5 | Inspection | Mike T. | Q1 quarterly. Same list. Belt tension adjusted. | Fan 4.3 A; cap 40/5 reads 39.6/4.9 | none | 0 | R-410A | 1.5 | 0 | J-10740 | No | 2026-06-01 | usedeepsel.com/commercial-hvac-maintenance-checklist
2026-04-14 | AND-01 | Anderson, Mark | 4TTR4036 | Maintenance | Dave R. | Spring tune-up. Condenser coil washed, contactor and capacitor checked, drain line flushed and treated, charge verified by subcooling. | ΔT 19 F; SC 10 F; SH 12 F; suction 121 psi; head 288 psi; cap 45/5 reads 44.6/4.8; comp 9.6 A | Filter 20x25x1 | 0 | R-410A | 1.25 | 0 | J-10802 | Yes | 2026-10-15 | usedeepsel.com/ac-maintenance-checklist
2026-04-21 | CAS-01 | Castillo, Rosa | 24ACC636A003 | Repair | Mike T. | Spring tune-up found subcooling 3 F (target 10). Leak search: Schrader core on liquid line valve. Replaced core, weighed in refrigerant, retested. Gold discount applied. Refrigerant amount and type recorded for the EPA log. | SC 3 F before, 10 F after; suction 128 psi; head 292 psi; ΔT 18 F | Schrader core | 0.75 | R-410A | 2 | 231.2 | J-10815 | Yes | 2026-10-20 | usedeepsel.com/ac-maintenance-checklist
2026-04-22 | NGU-01 | Nguyen, An | ML17XP1-048 | Install | Mike T., Dave R. | Full system replacement: 4-ton heat pump and air handler, R-454B. New pad, disconnect, whip, 25 ft lineset, media cabinet. Factory charge plus 0.5 lb for lineset length. A2L sensor tested. Registered for 10-year parts. | Startup: SC 9 F; SH 11 F; ΔT 20 F; TESP 0.55 in WC; comp 11.2 A | Lineset 25 ft; pad; disconnect; media cabinet | 0.5 | R-454B | 7 | 8450 | J-10820 | No | 2026-10-22 | commissioning sheet in job folder
2026-05-06 | YOU-01 | Young, Brenda | 4TTR6036 | Maintenance | Dave R. | Spring tune-up. Coil washed, capacitor within 6% of rating, drain cleared, filter changed. Homeowner asked about the 10-year mark on the furnace; noted for fall. | ΔT 18 F; SC 9 F; cap 40/5 reads 38.4/4.9 (ok, watch); comp 10.1 A | Filter 20x25x1 | 0 | R-410A | 1.25 | 0 | J-10861 | Yes | 2026-11-06 | usedeepsel.com/ac-maintenance-checklist
2026-05-12 | WAL-01 | Walsh, Tom | XP25-036 | Maintenance | Dave R. | Spring heat-pump check in cooling. Coil washed, charge verified, media filter changed, surge protector indicator green. | ΔT 20 F; SC 11 F; SH 10 F; comp 8.9 A | Media filter 20x25x4 | 0 | R-410A | 1.25 | 0 | J-10877 | Yes | 2026-11-12 | usedeepsel.com/heat-pump-maintenance-checklist
2026-05-19 | GAR-01 | Garcia, Luis | 24VNA936A003 | Maintenance | Mike T. | Spring tune-up on variable-speed system. Coil washed, charge verified per Carrier chart, media filter changed, readings emailed to homeowner as requested. | ΔT 19 F at high stage; SC 12 F; comp 7.4 A high stage | Media filter 20x25x4 | 0 | R-410A | 1.5 | 0 | J-10893 | Yes | 2026-11-03 | usedeepsel.com/ac-maintenance-checklist
2026-06-01 | MBD-RTU1 | Millbrook Dental (Dr. Ortiz) | 48TCED08A2A5 | Inspection | Mike T. | Q2 quarterly. Contactor replaced (pitting noted in Q1), coils cleaned, filters changed, economizer checked. | Fan 6.0 A; comp 1 21.4 A; comp 2 20.9 A; ΔT cool 18 F | Contactor 40 A 3-pole; 4 filters 20x20x2 | 0 | R-410A | 2.25 | 0 | J-10930 | No | 2026-09-01 | usedeepsel.com/commercial-hvac-maintenance-checklist
2026-06-01 | MBD-RTU2 | Millbrook Dental (Dr. Ortiz) | 48TCEA06A2A5 | Inspection | Mike T. | Q2 quarterly. Filters changed, coils cleaned, drain cleared. | Fan 4.3 A; comp 16.8 A; ΔT cool 19 F | 4 filters 16x20x2 | 0 | R-410A | 1.5 | 0 | J-10930 | No | 2026-09-01 | usedeepsel.com/commercial-hvac-maintenance-checklist
2026-06-08 | BAK-01 | Baker, Janet | GSZ140361 | Maintenance | Dave R. | Summer agreement visit. Coil washed, charge verified, filter changed, drain treated. | ΔT 18 F; SC 9 F; cap 35/5 reads 34.8/4.9; comp 9.0 A | Filter 16x25x1 | 0 | R-410A | 1 | 0 | J-10951 | Yes | 2027-01-08 | usedeepsel.com/ac-maintenance-checklist
2026-06-16 | DAW-01 | Dawson, Phil | RP1436AJ1NA | Emergency | Mike T. | No-cool call, 96 F day. Run capacitor failed (reads 21 µF on 40). Replaced, fan and compressor amps normal. Bronze discount 10%. | Cap 40/5 read 21/4.6; after: comp 10.4 A, fan 1.1 A | Capacitor 40/5 µF | 0 | R-410A | 1 | 170.1 | J-10980 | No |  | photo of failed cap in job
2026-07-07 | ELL-01 | Ellis, Tanya | ML14XC1-036 | Repair | Dave R. | Water in secondary pan, float switch tripped. Primary drain clogged at trap. Cleared with nitrogen, flushed, added pan tablets. Silver discount 15%. | Drain clear; ΔT 19 F | Pan tablets | 0 | R-410A | 1 | 109.65 | J-11033 | No |  | photo of trap
2026-07-22 | PAT-02 | Patel, Raj | 4TTV8024 | Maintenance | Dave R. | Spring/summer tune-up (late; homeowner traveling). Coil washed, charge verified, filter changed. PAT-01 done same visit under J-11078. | ΔT 19 F; SC 10 F; comp 7.8 A | Filter 16x20x1 | 0 | R-410A | 1 | 0 | J-11079 | Yes | 2027-01-20 | usedeepsel.com/ac-maintenance-checklist
2026-07-22 | PAT-01 | Patel, Raj | 4TTV8036 | Maintenance | Dave R. | Summer tune-up. Coil washed, charge verified, filter changed. Inducer from Feb warranty job running quiet. | ΔT 20 F; SC 10 F; comp 9.9 A | Filter 20x25x1 | 0 | R-410A | 1 | 0 | J-11078 | Yes | 2027-01-20 | usedeepsel.com/ac-maintenance-checklist
2026-08-04 | WAL-01 | Walsh, Tom | XP25-036 | Repair | Mike T. | Intermittent no-cool. Contactor pitted, replaced. Gold discount 15%. | Contactor coil ok; contacts pitted; comp 9.1 A after | Contactor 30 A 1-pole | 0 | R-410A | 1 | 140.25 | J-11102 | No |  | photo of contactor
2026-09-01 | MBD-RTU1 | Millbrook Dental (Dr. Ortiz) | 48TCED08A2A5 | Inspection | Mike T. | Q3 quarterly. Belt checked, filters changed, coils rinsed, economizer verified, condensate drain cleared. | Fan 6.1 A; ΔT cool 18 F; belt tension ok | 4 filters 20x20x2 | 0 | R-410A | 1.75 | 0 | J-11160 | No | 2026-12-01 | usedeepsel.com/commercial-hvac-maintenance-checklist
2026-09-01 | MBD-RTU2 | Millbrook Dental (Dr. Ortiz) | 48TCEA06A2A5 | Inspection | Mike T. | Q3 quarterly. Same list. Belt replaced (glazed). | Fan 4.4 A; ΔT cool 19 F | Belt A-40; 4 filters 16x20x2 | 0 | R-410A | 1.5 | 0 | J-11160 | No | 2026-12-01 | usedeepsel.com/commercial-hvac-maintenance-checklist