Free checklist from Deepsel · usedeepsel.com/furnace-maintenance-checklist · Version: September 2026 · Built on ANSI/ACCA 4 QM furnace tasks plus manufacturer service literature. Targets are typical field values; the rating plate and the manufacturer's instructions always win. For trained technicians.

# Furnace Maintenance Checklist · Fall Heating Visit

| Customer |  | Date |  |
| --- | --- | --- | --- |
| Service address |  | Technician |  |
| Make / model / serial |  | Age (years) |  |
| Fuel and type | ☐ Natural gas ☐ Propane ☐ Electric ☐ Oil · ☐ 80% ☐ 90%+ condensing | Stages | ☐ Single ☐ Two ☐ Modulating |
| Ignition / filter size | ☐ Hot surface ☐ Spark ☐ Standing pilot · Filter(s): ______________ | Agreement | ☐ Yes, tier: ______ ☐ No |
| This visit counts as | ☐ Heating visit, 2 of 2 ☐ Heating visit, 1 of 2 ☐ One-time tune-up |  |  |

## 1. Before touching anything

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Ambient CO in the living space, furnace running | 0 ppm. 1 to 9: find the source. 35+: stop and ventilate. 100+: evacuate, call 911 | ______ ppm |
| ☐ | Combustibles and stored items clear of cabinet and vent | Clearances per rating plate; 24" front service clearance | ☐ OK ☐ Corrected |
| ☐ | Gas leak check: unions, drip leg, valve, flex connector | Chloride-free soap solution or electronic detector. Never a flame | ☐ No leaks ☐ Leak found |
| ☐ | Watch the sequence of operation on a call for heat | Inducer, pressure switch closes, igniter warm-up, gas valve, flame proved, blower after delay | ☐ Normal ☐ Fault: ______ |

## 2. Combustion side (gas furnaces)

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Heat exchanger: mirror or borescope, flame watch at blower start, then combustion analysis | No cracks, rust-through or bulges. Flame must not move when the blower starts. CO stays stable with the blower running | ☐ Pass ☐ Suspect ☐ Condemn |
| ☐ | Burners and crossovers cleaned and aligned; flame check | Stable, quiet, blue, straight off the burner. Orange tips from dust are fine; yellow is not. No impingement | ☐ OK ☐ Cleaned ☐ Issue |
| ☐ | Hot surface igniter: visual, then cold resistance | No cracks or white spots. Silicon carbide commonly 40 to 90 Ω; silicon nitride far lower, about 11 to 17 Ω on common models. OL = replace. Compare to OEM | ______ Ω ☐ SiC ☐ SiN |
| ☐ | Flame sensor cleaned (fine steel wool or abrasive pad, wiped), burner ground checked | 0.5 to 10 µA DC depending on furnace; 2 to 6 µA common. Under about 1 µA: check rod, ground and wiring first | ______ µA |
| ☐ | Inlet gas pressure, furnace running | Per rating plate. Natural gas typically 4.5 to 10.0" w.c.; propane about 11 to 13" w.c. | ______ " w.c. |
| ☐ | Manifold pressure, each stage | Per rating plate. Natural gas 3.2 to 3.8" w.c., set 3.5; propane 9.7 to 10.3" w.c., set 10.0 | High ______ Low ______ |
| ☐ | Inducer: amps, bearings, wheel, collector box | Amps within nameplate; no water, rust or debris in the housing | ______ A ☐ OK |
| ☐ | Pressure switch: tubing pulled and blown clear, port clear | Open with inducer off, closed with inducer on; no water or kinks in the tubing | ☐ OK Set ______ " w.c. |
| ☐ | Limit switch and flame rollout switches | Continuity, no jumpers, mounted tight. Rollouts are often manual reset; note the type | ☐ OK ☐ Replaced |
| ☐ | Combustion analysis after 10 minutes of run, each stage | 80% induced draft, natural gas: O2 7 to 9%, CO2 6.5 to 8%, stack 325 to 400 °F, draft -0.02 to -0.04" w.c. CO air-free under 100 ppm; 100 to 400 repair; over 400 shut it down | O2 ____ % CO2 ____ % Stack ____ °F Draft ____ CO af ____ ppm |
| ☐ | Venting and combustion air | Connector rises toward the vent, joints tight, no rust streaks or condensate marks, termination clear, clearance to combustibles. Louvers and intake unobstructed | ☐ OK ☐ Issue |

## 3. Condensing furnaces (90%+), add these

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Condensate trap removed and flushed | Water flows from every port; hot water clears sludge. The trap is mandatory | ☐ Cleaned |
| ☐ | Drain line, condensate pump, float switch, neutralizer | Sloped, no double trap, vented after the trap; pump moves water, float shuts the furnace off. Condensate is acidic (pH about 3 to 5); replace spent media | ☐ OK ☐ Issue ☐ Media replaced |
| ☐ | PVC intake and exhaust | Joints sound, slope back to the furnace about 1/4" per foot, terminations clear and spaced | ☐ OK ☐ Issue |

## 4. Air side and electrical (all furnaces)

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Filter: size, fit, condition, airflow arrow | Replace if loaded. Record the size on the customer's record so the truck carries it next time | Size ______ ☐ Replaced |
| ☐ | Blower wheel and housing cleaned; motor amps; capacitor | Amps at or under nameplate FLA; capacitor within 6% of rated µF, no bulging | ____ A of ____ FLA · ____ µF of ____ |
| ☐ | Temperature rise, high fire, after 15 to 20 minutes | Within the rating plate range (for example 35 to 65 °F). Supply probe a few feet downstream, out of sight of the heat exchanger | Ret ____ Sup ____ Rise ____ °F · Plate ____ to ____ |
| ☐ | Total external static pressure | Most furnaces are rated 0.5" w.c. Return between filter and blower, supply between furnace and coil | Ret ____ + Sup ____ = ____ " w.c. |
| ☐ | Line and low voltage; connections; wire routing; board | Within nameplate; 24 V control; tight, no heat discoloration, no rubbing | ____ V / ____ V ☐ OK |
| ☐ | Thermostat, blower door switch, panels, humidifier if fitted | Full heat cycle on and off; door switch kills power; doors tight; pad, solenoid and drain | ☐ OK ☐ Pad replaced |

## 5. Electric furnace or heat strips

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Amps per stage against the kW rating | About kW × 1,000 ÷ volts. A 5 kW strip pulls about 20 A at 240 V; 10 kW about 40 A | S1 ____ S2 ____ S3 ____ A |
| ☐ | Sequencer or contactor staging; thermal limits; lugs; blower interlock; temperature rise | Stages close in order; limits read low ohms, never OL; lugs tight, breaker matches MCA; strips cannot run without the blower | ☐ OK ☐ Issue · Rise ____ °F |

## 6. Oil furnaces

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Oil filter and nozzle replaced; strainer cleaned; electrodes gapped; cad cell timed | Nozzle size, angle and pattern per burner spec. Burner shuts off within 45 seconds with the cad cell blocked | Nozzle ______ · ____ s |
| ☐ | Pump pressure, smoke test, combustion analysis | Pump commonly 100 to 150 psi per spec. Smoke near zero. Overfire draft about -0.02" w.c. Stack over 450 °F on a clean unit suggests oversizing | ____ psi · Smoke ____ · Draft ____ · O2 ____ % · CO ____ ppm · Stack ____ °F |

## 7. Findings, recommendations and sign-off

| Item | Condition found | Recommended action | Price after discount | OK? |
| --- | --- | --- | --- | --- |
|  |  |  |  | ☐ |
|  |  |  |  | ☐ |
|  |  |  |  | ☐ |

Overall: ☐ Safe to operate   ☐ Safe, repairs recommended   ☐ Unsafe, shut down and tagged (reason: ______________________________)

| Technician signature |  | Customer acknowledgement |  |
| --- | --- | --- | --- |
| Next visit due |  | Service sticker applied | ☐ Yes |
| Readings entered in the agreement record | ☐ Yes | Filter size on record | ☐ Yes |

File this sheet with the customer's maintenance agreement record. Next year's tech compares against these readings, and the completed visit is what the customer paid for. Free companions: the HVAC maintenance agreement template and the agreement tracking spreadsheet at usedeepsel.com.