Free checklist from Deepsel · usedeepsel.com/generator-maintenance-checklist · Version: October 2026 · Intervals and specs from the Generac, Kohler, Cummins, Briggs & Stratton and Champion owner's, installation and service manuals listed on the web page; commercial items from NFPA 110. The manual and nameplate for the unit in front of you override every number printed here. For trained technicians.

# Generator Maintenance Checklist · Standby Generator Service Visit

| Customer |  | Date |  |
| --- | --- | --- | --- |
| Service address |  | Technician |  |
| Make / model / serial |  | kW · install date |  |
| Fuel and cooling | ☐ Natural gas ☐ LP vapor ☐ Diesel · ☐ Air-cooled ☐ Liquid-cooled | Run hours as found |  |
| Transfer switch | Make / model / amps: ______________ ☐ Service rated · Load modules: ______ | Agreement | ☐ Yes, tier: ______ ☐ No |
| This visit counts as | ☐ Annual visit ☐ Visit 1 of 2 ☐ Visit 2 of 2 ☐ Post-outage service ☐ One-time service · Interval due: ☐ Yearly ☐ 2-year / Schedule A ☐ 4-year / Schedule B ☐ Hours: ______ |  |  |

How to use this sheet: sections 1 to 6 on every air-cooled home standby visit. Appendix A adds the liquid-cooled items. Appendix B adds the items for emergency and legally required systems under NFPA 110. Appendix C is the interval and spec reference by manufacturer. Write a number in every reading cell; next year's tech compares against it.

## 1. Before touching anything

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Controller as found: mode, active alarms and warnings, maintenance messages, run hours, last exercise | In AUTO with no active alarm. Write down every message before clearing it | Mode ______ · Alarms ______________ |
| ☐ | Exercise timer set and running | Generac air-cooled: weekly, biweekly or monthly, about 5 min · Kohler RCA: weekly, 20 min · Cummins: 1 to 20 min, default monthly 5 min · Champion: 15 min, fixed | Day / time ______ · Freq ______ |
| ☐ | Site: plants, stored items, water | Shrubs and tall grass cleared to 3 ft from the louvers (Generac). Nothing stacked against or built over the enclosure. No sprinkler, roof runoff, downspout or sump discharge aimed at the unit (Generac) | ☐ OK ☐ Corrected ☐ Reported |
| ☐ | Clearances against the installation manual (NFPA 37: 5 ft from combustible walls and wall openings unless the unit is fire-tested for less) | Generac (SwRI-listed): 18 in back, 5 ft from openings, 3 ft front and ends, 5 ft above · Cummins: 60 in from openings, 18 in one side · Briggs: 18 in, 5 ft from openings · Champion: 17.7 in back, 5 ft from windows · Kohler RCA: 4 ft clear of plants at the exhaust end, intakes 10 ft | Wall ____ · Opening ____ · ☐ OK |
| ☐ | Signs and emergency shutdown (2023 NEC jurisdictions) | Sign at the outdoor emergency disconnect showing the generator disconnect or shutdown location (702.7(A)); shutdown device outside the house marked "Generator Emergency Shutdown" (445.19(C)) | ☐ OK ☐ Missing |
| ☐ | Enclosure interior: nests, insects, debris, chewed wiring, corrosion | Base frame, brackets, alternator, fuel system and fasteners free of corrosion (Generac) | ☐ Clean ☐ Cleaned ☐ Damage: ______ |
| ☐ | CO alarms in the house | Installed and working on each level of the building near the generator (Kohler prestart check) | ☐ Present ☐ Reported |
| ☐ | Unit disabled for service | Controller OFF, controller fuse out (Generac 7.5 A), charger power off, negative battery cable off first | ☐ Done |

## 2. Engine

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Oil level and condition before draining | Between the marks. Note sludge, water, fuel smell or a level above full | ☐ OK ☐ Low ☐ Contaminated |
| ☐ | Oil and filter changed (when due, see Appendix C) | Oil grade and quantity from the manual; level checked on the dipstick after a short run; filter gasket oiled, hand-tight plus the manual's turn | Oil ______ · Qty ______ · ☐ Filter |
| ☐ | Air filter | Housing cleaned; element replaced when due or when loaded | ☐ OK ☐ Replaced |
| ☐ | Spark plugs: condition, gap, torque | Generac 10 to 18 kW 0.020 in, 20 to 26 kW 0.040 in · Kohler RCA 0.030 in · Briggs 0.030 in · Champion 22 kW 0.024 to 0.035 in · Cummins (2025 manual) 0.015 to 0.023 in. Torque per manual (Generac 18.4 ft-lb; Kohler and Cummins 18 to 22 ft-lb) | Gap ______ · ☐ Replaced |
| ☐ | Valve clearance, engine cold (engines without hydraulic lifters) | Generac 10 kW and 20 to 26 kW: 0.002 to 0.004 in (not on 14/18 kW Guardian or Next Generation) · Briggs: intake 0.004 to 0.006 in, exhaust 0.007 to 0.008 in | In ______ Ex ______ · ☐ n/a |
| ☐ | Breather hose, oil cooler fins, engine and exhaust leaks, exhaust outlet clear of combustibles | Kohler 20/26 kW: oil cooler yearly or 150 h · Briggs: oil cooler fins annually · Kohler: exhaust leaks and obstructions weekly | ☐ OK ☐ Issue |

## 3. Fuel system

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Leak test, supply to regulator, every connection | Non-corrosive leak detection fluid; it must not be blown away or form bubbles (Generac). Never a flame | ☐ No leaks ☐ Leak at ______ |
| ☐ | Flexible fuel line, shutoff valve, sediment trap | Flex line inspected, replaced as necessary (Kohler: quarterly). Sediment trap cleaned per local code (Generac) | ☐ OK ☐ Trap cleaned |
| ☐ | Fuel pressure at the generator inlet, full load, all gas appliances on | Generac: NG 3.5 to 7.0, LP 10 to 12 in wc · Kohler 14/20 RCA minimum: NG 5 to 11, LP 7 to 11 · Cummins: NG 3.5 to 10, LP 6 to 10, never above 10 · Briggs: NG 3.5 to 7, LP 11 to 14 · Champion: NG 5 to 7, LP 10 to 12 | Static ______ · Running ______ in wc |
| ☐ | LP tank level and regulator vent | Tank level written down (Kohler: main tank level weekly) | ______ % · ☐ n/a |

## 4. Battery and charger

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Battery: date code, case, terminals cleaned and tightened, electrolyte level on unsealed batteries | Distilled water only (Generac). Kohler: clean and tighten terminals, electrolyte and specific gravity yearly | Date code ______ · ☐ Cleaned |
| ☐ | Battery matches the spec | Generac: Group 26R 540 CCA wet or Group 35 AGM 650 CCA · Cummins: Group 51R, 450 CCA · Briggs: 540 CCA, 800 CCA below 30°F · Champion 22 kW: two 12 V Group 26, 540 CCA | Group ______ · Rated CCA ______ |
| ☐ | Voltage at rest; load or conductance test | Write the measured CCA next to the rated CCA, and compare with last visit | ______ V · ______ CCA |
| ☐ | Battery charger output and charge rate | Charger powered and charging (Kohler: monthly). Generac: no external chargers | ☐ OK ☐ Fault |

## 5. Enclosure, alternator and wiring

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Intake and discharge louvers, air ducts, enclosure interior | Clear and clean (Generac before each use when running; Kohler: air ducts yearly, enclosure interior quarterly) | ☐ OK ☐ Cleaned |
| ☐ | Wiring: abrasion where it moves, control and power connections | Kohler: abrasion every 6 months, connections tightened yearly · Briggs: circuit breaker torques every 100 h or annually | ☐ OK ☐ Tightened |
| ☐ | Brushes and slip rings (where fitted) | Kohler: brushes and collector ring yearly or 300 h (dealer) · Cummins: clean slip rings at 24 h or 6 months (as printed in Table 13) | ☐ OK ☐ Cleaned ☐ n/a |
| ☐ | Winding insulation resistance | Kohler: every 3 years (dealer), SCR assembly or rectifier and load leads disconnected | ______ MΩ · ☐ Not due |

## 6. Run test, transfer test and return to service

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Start and run unloaded; check for leaks, noise, vibration, warnings | Starts without cranking faults; no oil, fuel or exhaust leak | ☐ OK ☐ Issue |
| ☐ | Output voltage and frequency, no load | Against the nameplate (240 V, 60 Hz on single-phase home units) and last visit's reading | L1-L2 ____ V · L1-N ____ · L2-N ____ · ____ Hz |
| ☐ | Simulated outage: open the utility disconnect at the transfer switch (not a subpanel breaker) | Generac air-cooled: starts when utility drops below 65% of nominal after a 5 s delay, transfers after the warm-up (5 s; longer under Cold Smart Start) · Cummins: complete system test every 200 h or 2 years | Start ____ s · Transfer ____ s |
| ☐ | Under house load: amps per leg, voltage, frequency; load modules shed and restore | Amps under the rated maximum load current on the data label | L1 ____ A · L2 ____ A · ____ V · ____ Hz |
| ☐ | Utility restored: retransfer, cool-down, shutdown | Retransfers and runs its cool-down without alarms | ☐ OK |
| ☐ | Returned to service | AUTO; generator breaker ON; utility ON; exercise set; maintenance reminder reset (Kohler RDC2 maintenance timer, Champion hour meter, Cummins service LED) | ☐ AUTO ☐ Breakers ☐ Reset |

## 7. Findings, recommendations and sign-off

| Item | Condition found | Recommended action | Price after discount | OK? |
| --- | --- | --- | --- | --- |
|  |  |  |  | ☐ |
|  |  |  |  | ☐ |
|  |  |  |  | ☐ |

Overall: ☐ Ready to run in AUTO   ☐ Ready to run, repairs recommended   ☐ Not ready, left OFF (reason: ______________________________)

| Technician signature |  | Customer acknowledgement |  |
| --- | --- | --- | --- |
| Next service due (date or hours) |  | Run hours as left |  |
| Readings entered in the agreement record | ☐ Yes | Parts used (oil, filters, plugs, battery) |  |

File this sheet with the customer's maintenance agreement record. Manufacturers ask owners to keep maintenance records for warranty support, and next year's tech compares against these readings.

## Appendix A: Liquid-cooled units, add these

Generac Protector gaseous and diesel, Kohler RCL and similar liquid-cooled sets, on top of sections 1 to 6.

| ✓ | Task | Target / what to look for | Reading / result |
| --- | --- | --- | --- |
| ☐ | Coolant level, condition and freeze protection; hoses and clamps | Kohler RCL: condition, protection, hoses and clamps every year before cold weather · Generac: 40 to 60% ethylene glycol (Peak Fleet-Charge 50/50); never propylene glycol; never mix types or brands | Freeze point ______ °F · ☐ Hoses OK |
| ☐ | Coolant drained and flushed (when due) | Generac Protector gaseous and diesel: every 2 years or 250 h · Kohler RCL: 1,000 h, or 5,000 h or 5 years with long-life coolant | ☐ Done ☐ Not due |
| ☐ | Radiator exterior and air path | Clear of debris (Kohler RCL: every 100 h; Generac: daily while running) | ☐ OK ☐ Cleaned |
| ☐ | Belt condition and tension | Generac: every year or 125 h · Kohler RCL: every 1,000 h | ☐ OK ☐ Adjusted ☐ Replaced |
| ☐ | Oil and filter (when due) | Generac Protector 4.5 L: after 25 h, then every year or 125 h · Kohler RCL: every 150 h, 10W-30 above 0°F, 5W-30 below · Generac diesel: after 30 h, then every 2 years or 250 h | Oil ______ · Qty ______ |
| ☐ | Spark plugs (gaseous) or fuel filter and water drain (diesel) | Generac 4.5 L plugs: every 2 years or 250 h · Kohler RCL plugs: 400 h and 1,500 h · Generac diesel: drain fuel filter daily while running, replace element every 2 years or 250 h | ☐ Done ☐ Not due |
| ☐ | Block heater and battery heater working (cold climates) | Warm to the touch with the unit at rest | ☐ OK ☐ n/a |
| ☐ | Long-interval items | Generac: tighten critical fasteners every 1,000 h; diesel valve clearance, injection valve pressure and pump timing every 1,000 h · Kohler RCL: fuel system, regulator pressure, exhaust and wiring every 2,000 h | Hours ______ · ☐ Not due |
| ☐ | Exercise set | Generac Protector: weekly, about 12 min · Kohler RCL: weekly or every other week, 20 min | ☐ Set |

## Appendix B: Emergency and legally required systems (NFPA 110)

For systems under NEC Article 700 or 701 and NFPA 110 Chapter 8 (2025 edition section numbers; health care surveys use the 2010 edition). Home standby systems under NEC Article 702 are not covered by NFPA 110. The authority having jurisdiction sets the final schedule.

| ✓ | Task | Requirement | Reading / result |
| --- | --- | --- | --- |
| ☐ | System level, class and the written schedule on site | Level 1: failure could cost lives or cause serious injury · Level 2: less critical (4.4.1, 4.4.2) · written maintenance and test schedule (8.3.3) | ☐ Level 1 ☐ Level 2 · Class ______ |
| ☐ | Inspection log reviewed since last visit | Level 1 inspected weekly; Level 2 visually inspected at least monthly; automated monitoring may substitute for the weekly inspection (8.4.1, 8.4.10) | ☐ Complete ☐ Gaps: ______ |
| ☐ | Monthly exercise under load | At least 30 min (8.4.2). Diesel: manufacturer's minimum exhaust gas temperature or at least 30% of standby nameplate kW. Spark-ignited: available EPSS load (8.4.2.1) | ______ % load · ______ min · Exhaust ______ °F |
| ☐ | Annual load bank (diesel sets that miss the monthly load) | At least 50% of nameplate kW for 30 continuous min, then at least 75% for 1 continuous hour; 1.5 h total (8.4.2.4) | ☐ Done ______ ☐ Not required |
| ☐ | Transfer switches | Operated monthly, primary to alternate and back (8.4.6); test started from the ATS test switch or by opening a normal breaker, rotating ATSs (8.4.3); maintenance: connections, overheating and contact erosion, dust and dirt, contacts (8.3.4) | ☐ OK ☐ Issue ______ |
| ☐ | Time delays | Start at least 1 s; restoration to normal at least 5 min; shutdown at least 5 min (8.4.5) | Start ____ · Retransfer ____ · Cool-down ____ |
| ☐ | Starting batteries | Level 1 inspected weekly, Level 2 monthly (8.3.6). Maintainable: specific gravity recorded monthly. Sealed: conductance, ohmic, carbon pile load or cranking voltage drop test monthly. Defective batteries replaced immediately | SG / test ______ · ☐ Replaced |
| ☐ | Fuel quality test | At least annually, ASTM standards or the manufacturer's recommendations (8.3.7) | Date ______ · ☐ Pass |
| ☐ | Level 1 circuit breakers | Main and feed breakers between the EPS and the transfer switch load terminals exercised annually with the EPS off (8.4.7) | ☐ Done ☐ n/a |
| ☐ | Level 1 36-month test | At least once every 36 months, for the class duration; may end after 4 continuous hours (8.4.9) | Last ______ · Next ______ |
| ☐ | Records | Every inspection, test, exercise, repair and modification: date, servicing personnel, unsatisfactory conditions and corrective action including parts, retest; available to the AHJ on request (8.5) | ☐ Entered |

## Appendix C: Interval and spec reference by manufacturer

From the manuals listed on usedeepsel.com/generator-maintenance-checklist (Generac Guardian 10 to 26 kW owner's manual A0001846499 Rev. C; Kohler TP-7092 and TP-7093; Cummins A062J680 Issue 7, 2025; Briggs & Stratton 80106286 Rev. C; Champion 22 kW model 100304). Service is due at the hours or the calendar interval, whichever comes first.

| Item | Generac Guardian 10 to 26 kW | Kohler 14/20/26 RCA | Cummins Quiet Connect | Briggs & Stratton 17 to 26 kW | Champion 22 kW |
| --- | --- | --- | --- | --- | --- |
| Break-in oil change | 25 h | Not on schedule | 25 h and 100 h | Not on schedule | 5 h |
| Oil and filter | 2 years or 200 h; 1 year or 100 h below 40°F or continuous above 85°F | 14 kW: oil 1 year or 100 h, filter 1 year or 200 h · 20/26 kW: 1 year or 150 h · 26 kW extended-life oil: 2 years or 300 h | 200 h or 2 years | 100 h or annually | 2 years or 100 h |
| Oil type · capacity | SJ/SL or better; Generac 5W-20 after break-in · 1.1 / 2.2 / 1.9 qt (10 / 14–18 / 20–26 kW) | 5W-30 or 10W-30 synthetic · 1.9 qt (14 kW), 2.0 qt (20/26 kW) | Full synthetic SN, 5W-30 (0W-30 below 0°F) · 2.4 qt | 5W-30 full synthetic · 78–80 oz | 0W-40 full synthetic · 2.0 qt |
| Air filter | 4 years or 400 h | Check 150 h, change 300 h or yearly | 200 h or 2 years | 100 h or annually | Inspect 2 years or 100 h |
| Spark plugs · gap | 4 years or 400 h · 0.020 in (10–18 kW), 0.040 in (20–26 kW) | 300 h or yearly · 0.030 in | No interval listed · 0.015–0.023 in | 100 h or annually · 0.030 in | Inspect 2 years or 100 h · 0.024–0.035 in |
| Valve clearance | 25 h, then 4 years or 400 h · 0.002–0.004 in · none on 14/18 kW Guardian or Next Generation | Not on schedule | 25 h, 100 h, then 200 h (authorized tech) | Every 100 h · intake 0.004–0.006, exhaust 0.007–0.008 in | 2 years or 100 h (dealer) |
| Battery | Check 2 years or 200 h · 26R 540 CCA or 35 AGM 650 CCA | Charger monthly; terminals, electrolyte yearly | Every 200 h · 51R 450 CCA | 540 CCA; 800 CCA below 30°F | Terminals monthly · two Group 26, 540 CCA, 24 V |
| Fuel pressure, in wc | NG 3.5–7.0 · LP 10–12 | Minimum NG 5–11 · LP 7–11 (14/20 kW) | NG 3.5–10 · LP 6–10 · max 10 | NG 3.5–7 · LP 11–14, full load | NG 5–7 · LP 10–12, full load |
| Exercise | Weekly, biweekly or monthly · about 5 min | Weekly · 20 min | 1–20 min · default monthly, 5 min | Set at controller | 15 min, fixed |
| Oil check while running | Every 24 h, 30-minute shutdown | Every 8 h (14/20 kW), 24 h (26 kW) | Every 24 h | Every 8 h or daily | Every 24 h |

Keep this sheet with the equipment record. The readings in sections 1 to 6 are the baseline the next visit compares against. The matching maintenance agreement templates and a free visit-tracking sheet are at usedeepsel.com.