Free checklist from Deepsel · usedeepsel.com/heat-pump-maintenance-checklist · Version: September 2026 · Follow the manufacturer's service instructions and your own safety training. Refrigerant work requires EPA Section 608 certification.

# Heat Pump Maintenance Checklist

One sheet per outdoor unit. Use the cooling block in spring and the heating block in fall. Tick ☐ as you go, write every reading down, and give the customer a copy.

| Customer | [Name] · [Phone] · [Email] |
| --- | --- |
| Service address | [Street Address, City, State ZIP] |
| Date / technician | [Date] · [Technician] · Time in [__:__] · Time out [__:__] |
| Visit | ☐ Spring (cooling) ☐ Fall (heating) ☐ Both modes checked today · Agreement visit: ☐ 1 of 2 ☐ 2 of 2 ☐ Not on a plan |
| Outdoor unit | Make [____] Model [____] Serial [____] · Year [____] · ☐ Single stage ☐ Two stage ☐ Inverter / variable speed ☐ Cold-climate rated |
| Indoor unit | ☐ Air handler ☐ Ductless head(s), count [__] · Make [____] Model [____] Serial [____] |
| Filter size(s) | [__ x __ x __] · Qty [__] · ☐ Replaced today ☐ Washable, cleaned · Date written on filter ☐ |
| Refrigerant | Type ☐ R-410A ☐ R-454B ☐ R-32 ☐ R-22 ☐ Other [____] · Factory charge [____] oz · Line set length [____] ft |
| Auxiliary heat | ☐ Electric strips [____] kW, [__] stages ☐ Gas furnace (dual fuel) ☐ None · Thermostat make/model [____] |
| Conditions at visit | Outdoor dry bulb [____] °F · Indoor dry bulb [____] °F · Indoor wet bulb [____] °F · Weather ☐ Dry ☐ Rain ☐ Snow on ground |

## 1. Before you touch the equipment (every visit)

| ✓ | Task | Reading / note |
| --- | --- | --- |
| ☐ | Ask what the system has been doing: cold air in winter, ice on the outdoor unit, high bills, noise, short cycling. |  |
| ☐ | Thermostat set up as a heat pump; reversing valve terminal matches the unit (most units energize in cooling on O). | ☐ O ☐ B |
| ☐ | Auxiliary heat lockout and compressor lockout recorded. Utility programs want aux lockout at 35 °F or lower. | Aux lockout [____] °F · Compressor lockout [____] °F or ☐ none |
| ☐ | Return air and supply registers open and unblocked; filter rack sealed. |  |
| ☐ | Breaker and fuse sizes match the nameplate for the outdoor unit and the heat kit. | ODU [____] A · Heat kit [____] A |

## 2. Outdoor unit (every visit)

| ✓ | Task | Reading / target |
| --- | --- | --- |
| ☐ | Power off at the disconnect; confirm with a meter before opening the panel. |  |
| ☐ | Coil washed from the inside out; fins straight; no cottonwood, grass or dryer lint. | ☐ Clean ☐ Cleaned today ☐ Needs chemical clean |
| ☐ | Clearance: 2 ft to shrubs and fences on all sides, open above. Winter: unit sits above the snow line, no ice under the base. | Clearance [____] in · Riser height [____] in |
| ☐ | Base pan drain ports open so defrost water leaves the pan instead of freezing in it. |  |
| ☐ | Unit level and mounted solid; no rubbing lines; line set insulation intact. |  |
| ☐ | Fan blade, motor mount and guard: no cracks, no wobble; motor amps under nameplate. | Fan FLA [____] · Actual [____] A |
| ☐ | Contactor: no pitting, no chatter; all lugs tight, no heat discoloration. |  |
| ☐ | Run capacitor measured under load or with a meter, within 6% of the rating. | Rated [____] µF · Actual [____] µF |
| ☐ | Line voltage at the contactor, both legs. | [____] V (nameplate range [____]) |
| ☐ | Compressor running amps versus RLA; inverter units: read from the board or app. | RLA [____] · Actual [____] A |
| ☐ | Crankcase heater: warm shell with the compressor off, or ohms across the leads (no OL). | ☐ Warm ☐ [____] Ω ☐ None fitted |
| ☐ | Oil at brazed joints, service valves and Schrader cores; caps on and tight. | ☐ Dry ☐ Oil at [________] |
| ☐ | Defrost board: no burnt spots; sensor or thermostat clipped tight to the coil tube where the manual says. |  |

## 3. Indoor unit (every visit)

| ✓ | Task | Reading / target |
| --- | --- | --- |
| ☐ | Filter replaced or washed; size and date written on it. |  |
| ☐ | Indoor coil inspected with a light and mirror; cleaned if you can see dirt on the fins. | ☐ Clean ☐ Cleaned today ☐ Quote pull-and-clean |
| ☐ | Blower wheel and housing clean; motor amps under nameplate; ECM motor reports no faults. | Blower FLA [____] · Actual [____] A |
| ☐ | Blower capacitor (PSC motors) within 6% of rating. | Rated [____] · Actual [____] µF |
| ☐ | Drain pan flushed, trap primed, line cleared, pan treatment added; float switch tested by lifting it. | ☐ Float switch trips |
| ☐ | Total external static pressure: return plus supply, filter in place. | Return [____] · Supply [____] · TESP [____] in wc (target 0.5 or less) |
| ☐ | Heat kit lugs and sequencer terminals tight; no browned wire insulation. |  |
| ☐ | Ductwork: visible disconnects, crushed flex, missing insulation, return leaks in attic or crawl. |  |

## 4. Cooling-mode readings (spring visit, or any day above about 65 °F)

Run the system 10 to 15 minutes in cooling first. Use the manufacturer's charging chart. If the outdoor temperature is under 65 °F, note it and do the heating block instead of forcing a charge check.

| Reading | Measured | Target |
| --- | --- | --- |
| Outdoor dry bulb / indoor dry bulb / indoor wet bulb | [____] / [____] / [____] °F | Needed to read the chart |
| Suction pressure and suction line temperature | [____] psig · [____] °F | Per chart for these conditions |
| Superheat (fixed orifice) or subcooling (TXV / EEV) | SH [____] °F · SC [____] °F | Chart or nameplate; TXV subcool ±3 °F |
| Liquid pressure and liquid line temperature | [____] psig · [____] °F | Per chart |
| Supply air and return air dry bulb; temperature split | [____] / [____] · ΔT [____] °F | Delta T chart for the indoor wet bulb, ±3 °F |
| Reversing valve: cool call shifts the valve (click, pressures move) | ☐ Shifts | Suction-to-suction line difference 3 to 5 °F or less |
| Compressor amps / condenser fan amps / blower amps | [____] / [____] / [____] A | Under nameplate |
| Condensate flowing at the drain termination | ☐ Yes |  |

## 5. Heating-mode readings (fall visit)

Run the system 10 to 15 minutes in heating. Below 65 °F outdoors, treat the manufacturer's heat-mode chart as a guideline only. If the charge is in doubt, the accurate fix is recover, evacuate and weigh in the nameplate charge plus the line-set allowance.

| Check | Measured | Target |
| --- | --- | --- |
| Reversing valve shifts to heat; discharge gas goes to the indoor coil | ☐ Shifts | Line-to-line difference across the valve 3 to 5 °F or less |
| Suction pressure / liquid pressure in heat | [____] / [____] psig | Manufacturer heat-mode chart for outdoor and indoor DB |
| Discharge line temperature over outdoor ambient | [____] °F over | About 100 to 110 °F over ambient on a healthy charge |
| Supply air temperature at the nearest register | [____] °F | Varies with outdoor temp; record it and compare with last visit |
| Forced defrost: use the board's test pins or speed-up tap | ☐ Initiated | Valve shifts to cooling, outdoor fan stops, 24 V on O to C and on W2 to C, aux heat energizes |
| Defrost terminates and fan restarts | [____] min | Ends on coil temperature or the time limit (about 10 min max on most boards) |
| Defrost sensor or thermostat | [____] Ω at [____] °F | Resistance matches the manufacturer's table for that temperature |
| Aux heat stage 1 amps / stage 2 amps / stage 3 amps | [____] / [____] / [____] A | About 20 A per 5 kW at 240 V (kW × 1000 ÷ volts) |
| Sequencer staging: strips come on in order, blower runs before strips | ☐ Staged ☐ Interlock OK | Never strips without blower |
| Emergency heat from the thermostat: compressor off, strips on | ☐ Works |  |
| Aux heat drops out when the heat pump alone holds setpoint | ☐ Yes | Aux only on second stage call or during defrost |
| Condensate from the outdoor coil drains and does not pool under the unit | ☐ Yes |  |
| Crankcase heater energized with compressor off | ☐ Yes ☐ No heater |  |

## 6. Inverter, cold-climate and ductless units

| ✓ | Task | Reading / note |
| --- | --- | --- |
| ☐ | Manufacturer test run or diagnostic mode used for the mode check; error-code history read and cleared. | Codes [________] |
| ☐ | No gauges on the ports unless capacity is short after coils and filters are clean. Charge is by weight on these systems. | ☐ Not opened ☐ Opened, reason [________] |
| ☐ | Communicating controls: indoor and outdoor units see each other; firmware or dip switches per the manual. |  |
| ☐ | Ductless head: filters washed, blower wheel pulled or bibbed and cleaned, coil cleaned, drain pan and line flushed. | Heads done [__] of [__] |
| ☐ | Condensate pump (if fitted): reservoir cleaned, float tested, discharge line clear. |  |
| ☐ | Line hide and wall sleeve sealed; line set insulation intact where it enters the house. |  |
| ☐ | Outdoor unit on a wall bracket or riser above the local snow depth, drain path clear beneath it. | Height [____] in |

## 7. Findings and recommendations

| Item | What I found | Recommendation | Price after plan discount |
| --- | --- | --- | --- |

Overall condition: ☐ Good   ☐ Monitor   ☐ Repair recommended   ☐ Replacement conversation   · Refrigerant added: [____] oz of [____] (reason: [________])

## 8. Sign-off

| Technician | Signature [________________] · Date [____] |
| --- | --- |
| Customer | I received a copy of this checklist and the recommendations above. Signature [________________] · Date [____] |
| For the office | Visit logged against agreement ☐ · Plan tier [____] · Next visit due [____] · Filter size confirmed in customer record ☐ · Nameplate photo attached ☐ |

Targets on this sheet come from ACCA Standard 4 (residential maintenance), HVAC School, Trane, Bryant, ENERGY STAR and BPA's PTCS reference. The manufacturer's charging chart and service manual win any disagreement. Sources and the reasoning behind each line: usedeepsel.com/heat-pump-maintenance-checklist