Free cheat sheet from Deepsel · usedeepsel.com/hvac-cheat-sheet · Version: October 2026 · The rating plate, charging chart and installation instructions for the unit in front of you override every number on this sheet.

# HVAC Cheat Sheet · 1. Refrigerant PT chart (saturation pressure, psig)

| °F | R-22 | R-410A | R-32 | R-454B bubble | R-454B dew | °F | R-22 | R-410A | R-32 | R-454B bubble | R-454B dew |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -40 | 0.6 | 10.7 | 11.0 | 9.5 | 8.4 | 50 | 84.1 | 142.6 | 145.8 | 135.0 | 129.3 |
| -35 | 2.6 | 14.0 | 14.4 | 12.7 | 11.4 | 52 | 87.4 | 148.4 | 151.2 | 140.0 | 134.1 |
| -30 | 4.9 | 17.7 | 18.2 | 16.2 | 14.8 | 54 | 90.8 | 153.8 | 156.7 | 145.1 | 139.1 |
| -25 | 7.4 | 21.8 | 22.3 | 20.1 | 18.5 | 56 | 94.4 | 159.3 | 162.4 | 150.3 | 144.1 |
| -20 | 10.2 | 26.2 | 26.8 | 24.3 | 22.6 | 58 | 98.0 | 164.9 | 168.1 | 155.7 | 149.3 |
| -18 | 11.4 | 28.1 | 28.7 | 26.1 | 24.3 | 60 | 101.6 | 170.7 | 174.0 | 161.1 | 154.6 |
| -16 | 12.6 | 30.0 | 30.7 | 28.0 | 26.1 | 65 | 111.2 | 185.8 | 189.5 | 175.4 | 168.5 |
| -14 | 13.9 | 32.0 | 32.8 | 29.9 | 27.9 | 70 | 121.4 | 201.8 | 205.8 | 190.5 | 183.1 |
| -12 | 15.2 | 34.1 | 34.9 | 31.9 | 29.8 | 75 | 132.2 | 218.7 | 223.2 | 206.5 | 198.7 |
| -10 | 16.5 | 36.3 | 37.1 | 33.9 | 31.8 | 80 | 143.6 | 236.5 | 241.5 | 223.4 | 215.2 |
| -8 | 17.9 | 38.5 | 39.4 | 36.1 | 33.8 | 82 | 148.4 | 244.0 | 249.1 | 230.4 | 222.0 |
| -6 | 19.4 | 40.8 | 41.7 | 38.2 | 35.9 | 84 | 153.2 | 251.6 | 256.9 | 237.6 | 229.0 |
| -4 | 20.9 | 43.2 | 44.2 | 40.5 | 38.1 | 86 | 158.2 | 259.3 | 264.9 | 244.9 | 236.2 |
| -2 | 22.4 | 45.7 | 46.7 | 42.9 | 40.4 | 88 | 163.2 | 267.3 | 273.0 | 252.4 | 243.5 |
| 0 | 24.0 | 48.2 | 49.3 | 45.3 | 42.7 | 90 | 168.4 | 275.4 | 281.3 | 260.1 | 251.0 |
| 2 | 25.7 | 50.8 | 51.9 | 47.8 | 45.1 | 92 | 173.7 | 283.6 | 289.8 | 267.9 | 258.6 |
| 4 | 27.4 | 53.5 | 54.7 | 50.3 | 47.6 | 94 | 179.1 | 292.1 | 298.5 | 275.8 | 266.4 |
| 6 | 29.2 | 56.3 | 57.5 | 53.0 | 50.1 | 96 | 184.6 | 300.7 | 307.4 | 284.0 | 274.4 |
| 8 | 31.0 | 59.2 | 60.5 | 55.7 | 52.7 | 98 | 190.2 | 309.5 | 316.4 | 292.3 | 282.5 |
| 10 | 32.8 | 62.2 | 63.5 | 58.5 | 55.4 | 100 | 195.9 | 318.5 | 325.7 | 300.8 | 290.9 |
| 12 | 34.8 | 65.2 | 66.6 | 61.4 | 58.2 | 102 | 201.8 | 327.7 | 335.1 | 309.4 | 299.4 |
| 14 | 36.8 | 68.4 | 69.8 | 64.4 | 61.1 | 104 | 207.7 | 337.1 | 344.8 | 318.3 | 308.0 |
| 16 | 38.8 | 71.6 | 73.1 | 67.5 | 64.1 | 106 | 213.8 | 346.7 | 354.6 | 327.3 | 316.9 |
| 18 | 40.9 | 74.9 | 76.5 | 70.7 | 67.1 | 108 | 220.0 | 356.5 | 364.6 | 336.5 | 326.0 |
| 20 | 43.1 | 78.4 | 80.0 | 73.9 | 70.3 | 110 | 226.4 | 366.4 | 374.9 | 345.9 | 335.2 |
| 22 | 45.3 | 81.9 | 83.6 | 77.3 | 73.5 | 112 | 232.8 | 376.6 | 385.3 | 355.5 | 344.6 |
| 24 | 47.6 | 85.5 | 87.3 | 80.7 | 76.8 | 114 | 239.4 | 387.0 | 396.0 | 365.2 | 354.3 |
| 26 | 50.0 | 89.2 | 91.1 | 84.3 | 80.3 | 116 | 246.1 | 397.6 | 406.9 | 375.2 | 364.1 |
| 28 | 52.4 | 93.1 | 95.1 | 87.9 | 83.8 | 118 | 253.0 | 408.4 | 418.0 | 385.3 | 374.1 |
| 30 | 55.0 | 97.0 | 99.1 | 91.7 | 87.4 | 120 | 260.0 | 419.4 | 429.3 | 395.7 | 384.3 |
| 32 | 57.5 | 101.1 | 103.2 | 95.5 | 91.1 | 122 | 267.1 | 430.7 | 440.9 | 406.2 | 394.8 |
| 34 | 60.2 | 105.2 | 107.5 | 99.5 | 94.9 | 124 | 274.3 | 442.1 | 452.7 | 417.0 | 405.4 |
| 36 | 62.9 | 109.5 | 111.9 | 103.5 | 98.8 | 126 | 281.7 | 453.8 | 464.7 | 427.9 | 416.3 |
| 38 | 65.7 | 113.9 | 116.3 | 107.7 | 102.9 | 128 | 289.2 | 465.8 | 477.0 | 439.1 | 427.4 |
| 40 | 68.6 | 118.4 | 121.0 | 112.0 | 107.0 | 130 | 296.9 | 477.9 | 489.5 | 450.5 | 438.7 |
| 42 | 71.5 | 123.0 | 125.7 | 116.4 | 111.2 | 135 | 316.7 | 509.4 | 521.8 | 479.9 | 468.0 |
| 44 | 74.5 | 127.7 | 130.5 | 120.9 | 115.6 | 140 | 337.4 | 542.5 | 555.8 | 510.7 | 498.8 |
| 46 | 77.6 | 132.6 | 135.5 | 125.5 | 120.0 | 150 | 381.7 | 613.9 | 628.8 | 576.8 | 565.4 |
| 48 | 80.8 | 137.5 | 140.6 | 130.2 | 124.6 |  |  |  |  |  |  |

Which column: superheat uses the dew (vapor) temperature at suction pressure; subcooling uses the bubble (liquid) temperature at liquid pressure. R-454B's dew point runs 2.1 to 2.4°F above its bubble point. R-410A's glide is about 0.2°F, so its column is dew through 50°F and bubble from 52°F, as Chemours prints it. Sources: Chemours OPTXLPTAC-2 (4/25) and C-XL41PT-ENG (7/23), checked against Arkema Forane (05-2025).

## 2. Superheat and subcooling

| Reading | Formula | Where |
| --- | --- | --- |
| Superheat | Suction line temp − dew (vapor) saturation temp at suction pressure | Suction port; line at the outdoor unit (Goodman: 4 to 6 in from the compressor) |
| Subcooling | Bubble (liquid) saturation temp at liquid pressure − liquid line temp | Liquid service valve; line near the outdoor coil (Carrier), within 6 in of the unit (Rheem) |

Order: airflow first, then charge. ACCA 5 QI: airflow within the maker's tolerance before the charge is measured; superheat within ±5°F and subcooling within ±3°F of the maker's target, not added to the maker's own tolerance; superheat test typically at 55°F outdoor or above, subcooling at 60°F or above. TXV/EEV systems charge by subcooling; fixed orifice (piston) systems by superheat.

### TXV and EEV: subcooling to the rating plate (examples from current manuals)

| Unit | Target | Valid when | Otherwise |
| --- | --- | --- | --- |
| Carrier 26SCA5 AC, R-454B (06/24) | Rating plate value, ±3°F | Outdoor 70–100°F, indoor 70–80°F, 15 min run | Adjust for line length only; check later |
| American Standard 5A7A4 AC, R-454B (10/24) | Design subcooling corrected for line length and lift | Above 55°F outdoor; indoor 70–80°F; 20 min between adjustments | Weigh in; return in spring or summer |
| Lennox ML17KC2 AC, R-454B (03/26) | 2-ton 9.6°F · 3-ton 12.2 · 4-ton 13.6 · 5-ton 15.1, all ±1°F | 65°F outdoor and above | Below 64°F, weigh in |
| Goodman GLZS4BA HP, R-32 (12/23) | 8 ±1°F at the liquid valve (compressor superheat 16–19 ±1°F) | 60°F outdoor and above, cooling | Heating mode: by weight |
| Rheem (-)P14AY/(-)P15AY HP, R-454B | Charging chart inside the access panel | Cooling 55°F and up; heating 40–60°F; 15 min | Never below 40°F |

No label? 10–12°F is most common, up to 16°F on some systems; 10 ±3°F rule of thumb (HVAC School). TXV superheat at the evaporator outlet: about 5–15°F. R-454B and other blends: charge as liquid only.

### Fixed orifice (piston): target superheat, °F

|  | Indoor (return) wet bulb, °F |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OD °F | 50 | 52 | 54 | 56 | 58 | 60 | 62 | 64 | 66 | 68 | 70 | 72 | 74 | 76 | 78 |
| 55 | 7 | 10 | 12 | 15 | 18 | 21 | 24 | 27 | 30 | — | — | — | — | — | — |
| 60 | 5 | 8 | 10 | 13 | 16 | 19 | 22 | 25 | 28 | 31 | — | — | — | — | — |
| 65 | — | 4 | 8 | 11 | 14 | 17 | 19 | 22 | 25 | 28 | 31 | — | — | — | — |
| 70 | — | — | 5 | 8 | 11 | 14 | 17 | 19 | 22 | 25 | 28 | 31 | — | — | — |
| 75 | — | — | — | 5 | 7 | 10 | 14 | 18 | 21 | 24 | 28 | 31 | — | — | — |
| 80 | — | — | — | — | 4 | 7 | 10 | 12 | 16 | 19 | 23 | 26 | 29 | 33 | — |
| 85 | — | — | — | — | — | 4 | 7 | 10 | 14 | 18 | 21 | 24 | 28 | 30 | 32 |
| 90 | — | — | — | — | — | — | 4 | 8 | 11 | 14 | 18 | 22 | 25 | 28 | 31 |
| 95 | — | — | — | — | — | — | — | 4 | 8 | 13 | 16 | 20 | 23 | 26 | 29 |
| 100 | — | — | — | — | — | — | — | — | 6 | 10 | 13 | 18 | 21 | 25 | 29 |
| 105 | — | — | — | — | — | — | — | — | 4 | 7 | 11 | 15 | 20 | 24 | 28 |
| 110 | — | — | — | — | — | — | — | — | — | 4 | 9 | 13 | 18 | 23 | 28 |
| 115 | — | — | — | — | — | — | — | — | — | — | 6 | 12 | 16 | 21 | 26 |

American Standard 5A7A4 (R-454B) table, 11-AC49D1-1C-EN, every second wet-bulb column. Measure return wet bulb at the unit just before the coil and outdoor dry bulb. Add refrigerant to lower superheat, remove to raise it; wait 10 to 15 minutes after any change. Dash: no target, weigh the charge in. Carrier's R-410A piston table (24SCA4) gives the same 10°F at 95°F outdoor / 67°F wet bulb and runs about 2°F higher elsewhere, ±3°F.

## 3. HVAC troubleshooting chart: refrigerant-side readings

Clean filter and coils, airflow verified, the metering device known. A TXV holds superheat roughly steady until it fails or loses its full column of liquid; a piston does not.

### Fixed orifice (piston)

| Fault | Suction | Head | Superheat | Subcool | Amps | Air split |
| --- | --- | --- | --- | --- | --- | --- |
| Low charge | Low | Low | High | Low | Low | Low |
| Overcharge | High | High | Low | High | High | Norm/low |
| Low indoor airflow / low return temp | Low | Norm/low | Low | Norm/low | Norm/low | High |
| Dirty condenser | High | High | Norm/low | Norm/low | High | Low |
| Liquid line restriction | Low | Norm/low | High | High/norm | Low | Low |
| Oversized piston | High/norm | Norm/low | Low | Low | Low | Low |
| High return air temp | High | High | High | Norm/low | High | Low |

HVAC School diagnostic quick sheet. Low charge vs restriction: subcooling low on the undercharge, high on the restriction (look for a temperature drop or frost at the drier). Low airflow vs low charge: superheat low on airflow, high on charge.

### TXV / EEV (Rheem cooling-mode table)

| Fault | Head | Suction | Superheat | Subcool | Amps | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Overcharge | High | High | Low | High | High | Slight overcharge: suction and SH normal (HVAC School) |
| Undercharge | Low | Low | High | Low | Low | Slight undercharge: suction and SH normal |
| Liquid line restriction | Low | Low | High | High | Low | Looks like undercharge; subcooling normal to high (Goodman) |
| Low indoor airflow | Low | Low | Low | Low | Low | Air split high; fix airflow before charge |
| Dirty outdoor coil | High | High | Low | Low | High | Clean before judging charge |
| Low outdoor temp | Low | Low | High | High | Low | Below the maker's minimum, no charge check |
| Inefficient compressor | Low | High | High | High | Low | Goodman: low high side, high low side, low coil split, low amps, charge correct |
| TXV bulb charge lost (underfeed) | Low | Low | High | High | Low | Rule out a liquid line restriction first |
| Bulb loose or poorly insulated (overfeed) | High | High | Low | Low | High | HVAC School shows head and amps low; risk of floodback |

Restriction and head pressure: the charts disagree (Rheem lists it under both high and low head; Goodman and Trane under both). HVAC School: "In general, restrictions are in the liquid Line and will result in low head after sufficient run time." Subcooling high is the reading they agree on. Non-condensables: high head, fluctuating pressures, gurgle at the metering device. Goodman's test: shut down, let pressures equalize at least 15 minutes, compare pressure with the coldest coil's temperature on the PT chart; a higher saturation temperature than the coil means non-condensables. TXV check (Carrier): bulb in an ice bath for 1 minute, superheat should rise.

## 4. AC troubleshooting chart by symptom

| Symptom | Likely causes | Check first |
| --- | --- | --- |
| Nothing runs | Power, fuse or breaker, loose or broken wire, transformer, thermostat or wiring, control board, pressure-control lockout | Line voltage, then 24 V; board code; lockout resets by cycling power, then find the cause |
| Blower runs, outdoor unit dead | No 24 V at contactor coil (thermostat, LV wiring or fuse, safety open on loss of charge), contactor coil, no line voltage through contactor | 24 V across the coil; contactor closed: line voltage on load side |
| Fan runs, compressor does not | Run or start capacitor, start relay, loose connection, internal overload open, stuck compressor, open or grounded winding, low voltage | Capacitor µF; voltage at compressor; windings and ground. Hot overload: Rheem says wait at least 3 hours |
| Compressor hums, won't start | Run capacitor, stuck compressor; start capacitor, start relay, contacts | Run capacitor, then voltage at the terminals |
| Compressor runs, fan does not | Fan capacitor, fan overload, fan motor, loose lead, contacts; heat pump: defrost control or relay | Fan capacitor and windings; head climbs and compressor trips without the fan |
| Trips on overload or short cycles | Fan stopped, outdoor air blocked or recirculating, overcharge or non-condensables, low charge, voltage high or low, run capacitor, discharge restriction, high superheat, bearings | Running voltage within ±10% of nameplate (Rheem); coil and fan; charge |
| Runs, not enough cooling | Filter or indoor coil dirty, low airflow, low charge, restriction, inefficient compressor, wrong or failed valve, infiltration, undersized | Airflow (~400 CFM/ton), then the five refrigerant readings |
| Indoor coil or suction line ices | Low airflow, low charge, cooling below 65°F outdoor without low-ambient kit, moisture, restricted piston or strainer | Filter, blower, return; then charge. Below 32°F saturation the coil freezes |
| High head pressure | Dirty outdoor coil, fan off, recirculation, overcharge, non-condensables, high load | Coil, fan, clearances; non-condensables test; charge |
| Low head, high suction | Compressor valves or internal relief, TXV stuck open, heat pump reversing valve leaking | Goodman compressor test; reversing valve temperatures |
| Pressures and superheat swing | TXV hunting (superheat swings more than 10°F, Carrier), non-condensables | Bulb clamp and insulation; air distribution on the coil |
| Gurgle at expansion device | Non-condensables, undercharge | Subcooling at the condenser outlet and at the TXV inlet (Danfoss) |
| Compressor noisy | Overcharge, broken internals or valves, loose TXV bulb, hold-down bolts; 3-phase scroll reverse rotation | Superheat (floodback); bolts; phase rotation |
| Registers sweat | Low indoor airflow | Blower speed, filter, ducts |
| Too cool then too warm; uneven rooms | Thermostat faulty or badly placed, unbalanced airflow, infiltration | Thermostat location and wiring; dampers |

Combined from Carrier's air conditioner troubleshooting chart (24-25-8SM), Goodman's service problem analysis guide (RS6200006), Rheem's general troubleshooting guide (92-105074-04-17) and Trane's 4TWR6 fault matrix. Disconnect power before opening the unit: "Contactor may break only one side" (Rheem).

## 5. Heat pump troubleshooting chart

In heat mode the indoor coil is the condenser and the outdoor coil the evaporator. Heating readings diagnose; they do not set the charge (weigh in below the maker's minimum outdoor temperature and verify in cooling season).

| Fault, heating mode (Rheem) | Head | Suction | Superheat | Subcool | Amps |
| --- | --- | --- | --- | --- | --- |
| Overcharge | High | High | OK | High | High |
| Undercharge | Low | Low | OK or high | Low | Low |
| Liquid line restriction | Low | Low | High | High | Low |
| Low outdoor airflow | Low | Low | Low | Low | Low |
| Dirty indoor coil | High | High | Low | Low | High |
| Low indoor temperature | Low | Low | OK | High | Low |
| Inefficient compressor | Low | High | High | High | Low |
| Outdoor TXV bulb charge lost | Low | Low | High | High | Low |
| Outdoor bulb poorly insulated | High | High | Low | Low | High |

| Symptom | Likely causes | Check first |
| --- | --- | --- |
| Outdoor coil ices and stays iced | Defrost control or its power, defrost thermostat or sensor failed or loose, reversing valve not shifting, defrost relay welded (fan keeps running), low charge, blocked outdoor air, low indoor airflow | Force a defrost (below): valve shifts, fan stops, aux on. Sensor tight on the tube; Rheem sensor ~30,000 ohms at 35°F; Carrier: 24 V at T1 |
| Defrost runs long or leaves ice | Termination setting, sensor location, low charge, fan relay not stopping fan, thermostat satisfied mid-defrost, control or thermostat failed | Termination jumper, sensor, charge, fan relay |
| Runs, blows cool, low heat | Reversing valve, charge, non-condensables, inefficient or stuck compressor, outdoor fan stopped, coil dirty or frosted, restriction, open heat element or limit, defrost control | Supply temperature against normal (below); fan; valve; heating readings |
| Reversing valve stuck or leaking | No 24 V to solenoid, coil open, pilot or slide stuck, mid-position (high suction), internal leak (low head, high suction) | 24 V at solenoid; pull coil and listen for the click; raise head and cycle modes. Leak: true suction vs suction after the valve no more than 4°F apart (Goodman) |
| Trips on overload in heat | Dirty filter or indoor coil, indoor fan off, charge, non-condensables, valve mid-position, voltage, capacitor | Indoor airflow first: restricted indoor airflow is a primary cause of high head in heat (Trane) |
| Aux heat on far more than usual | Outdoor fan motor, low charge, compressor, defrost board stuck in defrost, valve stuck in cooling | Lennox: aux on more than about 30 minutes means call a tech. Aux during defrost is normal |

## 6. Heat pump defrost and what is normal

| Maker | Starts defrost | Interval | Ends | Limit | Force a test |
| --- | --- | --- | --- | --- | --- |
| Carrier time-temp | Thermostat closed (32 ±3°F) for set run time | 30/60/90 (120 some); factory 60 or 90 | ~65°F | 10 min | Short speed-up pins (jumper DFT if coil warm); remove at shift |
| Goodman | Sensor closed (~31°F) + heat call | 30/60/90 | ~75°F | 10 min (12 upgraded) | Jumper DFT-R, jump test pins; defrost within 21 s; 24 V C-O, W2-C |
| Lennox ML14XP1 | Thermostat closed, run time | 30/60/90; factory 90 | Thermostat opens | 14 min | Short TEST pins 2 s; remove within 5 s |
| Rheem (-)P14/P15 | Coil <35°F, 34 min run, ambient-coil calc | Demand | 70°F (50/60/80) | 14 min | Short and hold TEST pins with a heat call |
| Trane / Am. Std. | Change in air-to-coil ΔT | Demand | 47°F (70°F, J2 cut, ≤30°F) | <6°F: 12 min or 35°F every 3 h | Short FRC_DFT to TEST_COMMON 2 s |

Reversing valve terminal: O energized in cooling (Carrier, Goodman); B energized in heating (Rheem (-)P14/P15); on Trane's 4TWR6, B is the 24 V common. Match the thermostat's O/B setting to the outdoor unit's diagram. Normal: steam or fog in defrost; a whoosh at start and end; outdoor fan off and aux heat on in defrost; compressor pausing ~30 s in and out of defrost where the delay is enabled; light frost under 1/4 in that clears (Carrier); coil 10–20°F colder than outdoor air (Trane); defrost 5–15 min (Lennox), 3–5 min on demand defrost (Trane); supply air about 85–105°F, against 120–140°F from a gas furnace (Carrier, Trane).

## 7. Rules of thumb and formulas

| Reading | Rule of thumb (manufacturer data wins) |
| --- | --- |
| Evaporator saturation, cooling | 35°F below return air temperature ±5°F at 400 CFM/ton; 38–40°F below at 350 CFM/ton. Below 32°F saturation the coil will eventually freeze |
| Condensing saturation | 15–20°F above outdoor ±3°F on most modern systems. By efficiency: 30°F (6–10 SEER), 25°F (10–12), 20°F (13–15), 15°F (16+) |
| TXV superheat, evaporator outlet | 5–15°F (10 ±5) |
| Subcooling, TXV/EEV | Rating plate. Without one: 8–14°F typical, 10 ±3°F; 10–12°F most common, up to 16°F |
| Subcooling, fixed orifice | 5–23°F with load, usually 10 ±3°F; charge by superheat |
| Temperature split, cooling | 16–22°F return to supply; lower in high humidity |
| Airflow | 400 CFM/ton nominal; ACCA 5 QI: typically 350–450 CFM/ton |
| Total external static | 0.3–0.7 in wc on most systems |
| Example, 95°F outdoor, 80°F return | Evaporator ~45°F (40–50): R-410A 118–143 psig, R-454B dew 107–129 psig. Condenser 110–115°F: R-410A 366–392 psig, R-454B bubble 346–370 psig |

| To find | Formula |
| --- | --- |
| Sensible capacity, Btu/h | CFM × ΔT (°F) × 1.08 |
| Total capacity, Btu/h | 4.5 × CFM × (return enthalpy − supply enthalpy), enthalpy from wet bulb |
| Airflow from electric heat, CFM | (volts × amps × 3.413) ÷ (temperature rise × 1.08) |
| Airflow from a gas furnace, CFM | (gas input cu ft/h × Btu per cu ft × measured efficiency) ÷ (temperature rise × 1.08) |
| Gas input from the meter, cu ft/h | 3,600 × smallest dial size (cu ft) ÷ seconds for one revolution |
| Run capacitor under load, µF | 2,652 × start-winding amps ÷ volts across the capacitor |
| Conversions | 1 ton = 12,000 Btu/h · 1 W = 3.413 Btu/h · 1 kW = 3,413 Btu/h · 746 W = 1 hp · gas outlet pressure: natural gas 3.5 in wc, LP 11 in wc |

Sources: HVAC School, "The 5 Pillars of Residential A/C Refrigerant Circuit Diagnosis," "What Should My Subcooling Be?" and the HVAC Air / Refrigerant Diagnostic Quick Sheet; ANSI/ACCA 5 QI-2015 §4.1. Pressures from the chart on page 1. Full citations at usedeepsel.com/hvac-cheat-sheet.