## Filter slots
Unit ID | Building / site | Filter location | Nominal size (L x W x D) | Qty | Filter type | MERV | Brand / part no. | Interval (days) | Last changed | Next due | Days left | Status | Change-out pressure (in. w.g.) | Cost per filter | Filter cost per year | Responsible | Notes
EXAMPLE RTU-1 | Main St plaza | Filter rack, 4 filters | 20x25x2 | 4 | 2-inch pleated | 8 | Camfil 30/30 | 90 | 2026-06-14 | 2026-09-12 | -12 | Overdue | 1 | 9.5 | 154.1111 | Contractor | Change at 1.0 in. w.g. or quarterly, whichever first
EXAMPLE Furnace | 14 Oak Ave | At air handler, basement | 16x25x4 | 1 | 4-5 inch media | 13 | Aprilaire 213 | 365 | 2026-09-01 | 2027-09-01 | 342 | OK |  | 42 | 42 | Owner | Fan runs continuously, check at 6 months
EXAMPLE Apt 2B | Elm St fourplex | Return grille, hallway | 16x25x1 | 1 | 1-inch pleated | 11 | Filtrete 1000 | 60 | 2026-08-30 | 2026-10-29 | 35 | OK |  | 6 | 36.5 | Tenant | Two dogs
Formulas:
Last changed = IF([Unit ID]="","",IF(MAXIFS('Change log'!$A:$A,'Change log'!$B:$B,[Unit ID],'Change log'!$C:$C,"Replaced")=0,"",MAXIFS('Change log'!$A:$A,'Change log'!$B:$B,[Unit ID],'Change log'!$C:$C,"Replaced")))
Next due = IF(OR([Last changed]="",[Interval (days)]=""),"",[Last changed]+[Interval (days)])
Days left = IF([Next due]="","",[Next due]-TODAY())

## Change log
Date | Unit ID | Action | Pressure drop before (in. w.g.) | Pressure drop after (in. w.g.) | Condition removed | Fit and arrow OK | By | Reason | Cost | Days since previous replacement | Notes
2026-03-10 | EXAMPLE RTU-1 | Replaced | 0.95 | 0.28 | Heavy | Y | JM | Pressure drop | 38 |  | Spring startup
2026-06-02 | EXAMPLE Furnace | Checked and left in |  |  | Light | Y | Owner | Schedule
2026-06-14 | EXAMPLE RTU-1 | Replaced | 0.98 | 0.27 | Heavy | Y | JM | Pressure drop | 38 | 96 | Cottonwood season
2026-07-01 | EXAMPLE Apt 2B | Replaced |  |  | Heavy | Y | Tenant | Schedule | 6
2026-08-30 | EXAMPLE Apt 2B | Replaced |  |  | Moderate | Y | Tenant | Dirty | 6 | 60 | Wildfire smoke week
2026-09-01 | EXAMPLE Furnace | Replaced |  |  | Moderate | Y | Owner | Schedule | 42 |  | Media went gray at 10 months

## Intervals
Filter type | Interval the source states | Source
1-inch fiberglass | About 30 days | Carrier, All About Air Filters, https://www.carrier.com/residential/en/us/products/air-conditioners/air-conditioner-maintenance/all-about-air-filters/
1-inch pleated | Check monthly, change at least every 3 months | ENERGY STAR, https://energystar.gov/saveathome/heating-cooling
1-inch pleated | Makers typically recommend 60 to 90 days | EPA, Guide to Air Cleaners in the Home, https://www.epa.gov/indoor-air-quality-iaq/guide-air-cleaners-home
1-inch pleated | At least every 3 months; sooner with pets, smokers, construction, a continuously running fan | 3M Filtrete FAQ, https://www.filtrete.com/3M/en_US/filtrete/about-us/faq/
4- to 5-inch media | Every 12 months | 3M Filtrete FAQ, https://www.filtrete.com/3M/en_US/filtrete/about-us/faq/
4- to 5-inch media | At least annually; seasonally if the system heats and cools; 6 to 12 months on the F200 page | Honeywell Home, https://www.honeywellhome.com/us/en/support/media-air-filter-maintenance/
4- to 5-inch media | Annually; 6 months if the fan runs 24/7; MERV 16 every 6 months | Aprilaire FAQ, https://www.aprilaire.com/blog/aprilaire-air-purifiers-and-air-filters-faqs
Washable electrostatic | Vacuum every 30 to 45 days, rinse every 1 to 4 months | Air-Care, https://www.air-care.com/product-category/electrostatic-air-filters/
Electronic air cleaner cells | Clean twice a year with normal use | Honeywell Home, https://www.honeywellhome.com/blogs/support/electronic-air-filter-maintenance
Ductless mini-split screens | Every 2 weeks | Daikin operation manual, https://web-manual.dit-daikin.com/ra/en/cleaning_filters/
Commercial pleated in an air handler | Check quarterly at minimum; change at the maker's final resistance, 1.0 in. w.g. on Camfil 30/30, AQ13 and AAF PerfectPleat | ASHRAE/ACCA Standard 180 Table 5-2; Camfil, https://www.camfil.com/dam/files/1174/1322760/Product-Sheet-Farr-3030.pdf; AAF, https://sc82apps.aafintl.com/-/media/files/aaf/commercial-and-industrial/us-products/pleated-filters/perfectpleat-sc-m8/perfectpleat-sc-m8_prod_mark_sht_afp-1-202c-new.pdf

## How to use
HVAC filter change log, free from Deepsel. usedeepsel.com/hvac-filter-change-log-template. Version September 2026.
1. Filter slots tab: one row per filter position. A rack of four filters is one row with Qty 4. Delete the three EXAMPLE rows once you have your own.
2. Set Interval (days) per slot: 90 for a 1-inch pleated on ENERGY STAR's rule, 180 or 365 for 4- to 5-inch media, or whatever the Days since previous replacement column tells you after two changes.
3. Change log tab: one row per visit to a filter. Action Replaced sets Last changed on the slots tab; Checked and left in is the monthly check ENERGY STAR asks for. Keep the log sorted by date.
4. Next due, Days left and Status compute themselves. Status turns yellow at 14 days out and pink when overdue.
5. Pressure drop columns are for units with a filter gauge. Put the maker's final resistance in Change-out pressure on the slots tab and change the filter when the gauge reads it.
6. Formulas use MAXIFS, which needs Excel 2019 or Microsoft 365, and work in Google Sheets and LibreOffice.
Printable one-page-per-unit sheet (PDF, Word, Google Docs) and every other free checklist: usedeepsel.com/checklists