Free checklist from Deepsel · usedeepsel.com/hvac-inspection-checklist · Version: September 2026 · Not a substitute for the manufacturer's service instructions or safety training. One sheet per unit.

# HVAC Inspection Checklist

| Customer |  | Date / technician |  |
| --- | --- | --- | --- |
| Service address |  | Unit ___ of ___ · location | ☐ attic ☐ closet ☐ basement ☐ garage ☐ crawl ☐ yard ☐ roof · serves ________ |
| Reason | ☐ First visit on a new maintenance agreement ☐ Home sale (☐ buyer ☐ seller) ☐ Landlord / property manager ☐ Seasonal walk-through ☐ Other: ________ |  |  |

## 1. Nameplate capture (photograph the full data plate first)

| Field | Indoor unit (furnace / air handler / coil) | Outdoor unit (condenser / heat pump) |
| --- | --- | --- |
| Type · make · model | ☐ gas furnace ☐ air handler ☐ oil ☐ coil ☐ mini split head ________________________ | ☐ AC ☐ heat pump ☐ package ☐ mini split ________________________ |
| Serial · mfg date · age | ________________ · ______ · ____ yrs | ________________ · ______ · ____ yrs |
| Capacity | Input ______ · output ______ BTU/h · blower ____ ton | ____ tons (model digits 024 = 2, 036 = 3, 048 = 4, 060 = 5) |
| Refrigerant | Coil: ☐ R-410A ☐ R-454B ☐ R-32 ☐ R-22 ☐ ____ | ☐ R-410A ☐ R-454B ☐ R-32 ☐ R-22 ☐ ____ · charge ____ oz |
| Electrical (plate vs installed) | ____ V · MCA ____ · MOP ____ · breaker ____ A | ____ V · MCA ____ · MOP ____ · breaker ____ A |
| Filter · IAQ · thermostat | Filter nominal ______ · actual ______ · ☐ 1" ☐ 4" ☐ washable · at ☐ grille ☐ unit · qty __ ¦ UV bulb ______ ☐ humidifier ¦ Thermostat __________ ☐ smart ☐ manual |  |
| Photos taken | ☐ both data plates ☐ each unit overall ☐ filter rack ☐ disconnect and breaker ☐ drain and pan ☐ flue / vent ☐ line set ☐ every defect in Section 7 |  |

## 2. Safety (first; stop and report on any Fail)

| Check | Reading / target | Result |
| --- | --- | --- |
| CO in ambient air, at unit and at a supply register | ____ / ____ ppm. Typical home 0.5 to 5; investigate over 9; leave and report over 35 | ☐ Pass ☐ Flag ☐ Fail |
| Flue CO air free (analyzer, gas furnace) | ____ ppm · O2 ____ % · stable at 10 min ☐. Under 100 target; 400 or more = shut down | ☐ Pass ☐ Flag ☐ Fail ☐ N/A |
| Gas leak check: valve, unions, flex, drip leg | Detector sweep ☐ · bubble test on any hit ☐ · leak at: ________ | ☐ Pass ☐ Fail ☐ N/A |
| Venting / flue | Connected ☐ sloped ☐ no corrosion or holes ☐ clearances ☐ termination clear ☐ | ☐ Pass ☐ Flag ☐ Fail |
| Burner flame · rollout · heat exchanger (visible surfaces) | Flame ☐ blue, steady ☐ yellow / lifting · scorch marks ☐ · HX ☐ no visible cracks or rust-through ☐ suspected crack at ________ | ☐ Pass ☐ Flag ☐ Fail |
| Electrical: disconnect, breaker, wiring | Disconnect works ☐ · breaker ≤ MOP ☐ · no burnt or loose wiring ☐ · ground ☐ | ☐ Pass ☐ Flag ☐ Fail |
| Condensate · combustion air · CO alarm | Drain flows ☐ · float switch or secondary ☐ · pan rust or water ☐ · clearances and intake clear ☐ · CO alarm in home ☐ | ☐ Pass ☐ Flag ☐ Fail |

## 3. Cooling readings (running 10 minutes or more; record, do not adjust)

| Reading | Value / target | Result |
| --- | --- | --- |
| Return · supply · temperature split | Return ____ °F DB / ____ WB / ____ % RH · outdoor ____ °F · supply ____ °F · split ____ °F (18 to 22 at 45 to 55% RH; lower when humid; a low split is a finding, not a diagnosis) | ☐ Pass ☐ Flag |
| Compressor amps · fan amps vs plate | ____ A / RLA ____ ¦ ____ A / FLA ____ | ☐ Pass ☐ Flag |
| Run capacitor(s) · contactor | Herm ____ / rated ____ µF · fan ____ / rated ____ µF (within ±6%) · contactor ☐ clean ☐ pitted | ☐ Pass ☐ Flag |
| Refrigerant circuit (non-invasive unless charge is in question) | Suction line ____ °F · liquid line ____ °F. Gauges only if needed: ____ / ____ psig · SH ____ (orifice) · SC ____ (TXV) vs plate ____ · oil or frost at ______ | ☐ Pass ☐ Flag ☐ Suspected leak |
| Coils · line set · outdoor setting | Condenser ☐ clean ☐ dirty ☐ bent · evaporator ☐ clean ☐ dirty ☐ iced · line insulation ☐ ok ☐ missing · level ☐ · clearance ____ in | ☐ Pass ☐ Flag |

## 4. Heating readings (gas furnace or heat pump; record, do not adjust)

| Reading | Value / target | Result |
| --- | --- | --- |
| Ignition sequence · limit | Inducer ☐ · pressure switch ☐ · lights first try ☐ · retries ____ · high limit cycles during run ☐ yes ☐ no | ☐ Pass ☐ Flag |
| Manifold gas pressure vs plate | ____ in WC / plate ____ (natural gas about 3.5; LP about 10) | ☐ Pass ☐ Flag ☐ N/A |
| Temperature rise vs plate range | Return ____ · supply ____ · rise ____ °F · plate ____ to ____. Near the top means low airflow | ☐ Pass ☐ Flag |
| Flame sensor · blower · inducer | ____ µA (1 to 10, ideally 2 to 6) · blower ____ A / FLA ____ ☐ PSC ☐ ECM · inducer ____ A, rust or water ☐ | ☐ Pass ☐ Flag |
| Heat pump only | Reversing valve shifts ☐ · defrost board ☐ · strips ____ kW / ____ A · coil ice ☐ | ☐ Pass ☐ Flag ☐ N/A |

## 5. Airflow and ducts

| Check | Value / target | Result |
| --- | --- | --- |
| Total external static pressure | Return ____ · supply ____ · total ____ in WC vs plate max ____ (most residential equipment is rated 0.5; return at 0.4 or more is high) | ☐ Pass ☐ Flag |
| Filter as found · ducts · thermostat | Filter ☐ clean ☐ dirty ☐ collapsed ☐ missing ☐ wrong size · crushed or open runs ☐ · leaks at plenum ☐ · returns __ supplies __ · thermostat calls heat ☐ cool ☐ reads ____ vs ____ | ☐ Pass ☐ Flag |

## 6. Condition grade

| Grade | Label | Meaning |
| --- | --- | --- |
| 5 | Like new | Under 3 years old, every reading inside target, no findings. |
| 4 | Good | Inside targets; minor findings only (dirty filter, missing insulation, cosmetic rust). |
| 3 | Fair | Runs, but a reading is outside target or a wear part is near its limit. Repairs recommended. |
| 2 | Poor | Major component at risk, refrigerant leak, safety flag, or past median life with findings. |
| 1 | Replace / unsafe | Locked out, high CO, suspected cracked heat exchanger, failed compressor, or age × repair over $5,000. |
| This unit: ____ indoor ____ · outdoor ____ · ducts ____ (Good = 4 to 5, Fair = 3, Poor = 1 to 2) |  |  |

## 7. Findings and recommendations

| # | Finding (what, where, reading) | Priority | Photo | Estimate | Excluded |
| --- | --- | --- | --- | --- | --- |
| 1 |  | ☐ Safety ☐ Now ☐ Watch |  | $ | ☐ |
| 2 |  | ☐ Safety ☐ Now ☐ Watch |  | $ | ☐ |
| 3 |  | ☐ Safety ☐ Now ☐ Watch |  | $ | ☐ |

## 8. Age note and acknowledgement

Oldest major component ____ years (ASHRAE median: 15 for AC and heat pump, 18 for furnace). $5,000 rule: age ____ × repair quote $______ = $______; over $5,000 favors replacement. Refrigerant ☐ R-22 (not produced since 2020) ☐ R-410A (no new systems built since 2025) ☐ A2L.

Section 7 conditions existed on the inspection date; items marked pre-existing are excluded from any maintenance agreement until repaired and re-inspected. Readings were taken as found; nothing was cleaned, adjusted or added.

| Technician signature |  | Customer signature |  |
| --- | --- | --- | --- |
| Delivered · next step | ☐ printed ☐ emailed · photos ____ ¦ ☐ agreement offered ☐ repair estimate ☐ replacement estimate ☐ none |  |  |

Free from usedeepsel.com/hvac-inspection-checklist. Maintenance and tune-up versions and a matching equipment log: usedeepsel.com/checklists.