Free checklist from Deepsel · usedeepsel.com/hvac-maintenance-checklist · Version: September 2026 · Built from ANSI/ACCA Standard 4, Maintenance of Residential HVAC Systems. The manufacturer's service instructions govern where they differ. Refrigerant work requires EPA Section 608 certification.

# HVAC Maintenance Checklist

Residential split system: air conditioner or heat pump with a gas furnace or air handler. Part A is done on every visit, Part B on the spring (cooling) visit, Part C on the fall (heating) visit. Mark each line OK, Attn (works, but note it) or Fail (needs repair). Write the reading wherever a blank is printed.

| Customer | [Name] · [Phone] · [Email] | Service address | [Street, City, State ZIP] |
| --- | --- | --- | --- |
| Date · time in/out | [Date] · [In] to [Out] | Technician | [Name] |
| Visit type | ☐ Spring / cooling ☐ Fall / heating ☐ Both | Agreement | ☐ Member, plan [Tier], visit [1] of [2], plan year [Year] ☐ Non-member |
| Outdoor temp (shade) | [°F] | Indoor return air | [°F] dry bulb · [°F] wet bulb |

## Equipment (one checklist per system)

| Unit | Make and model | Serial | Year | Location |
| --- | --- | --- | --- | --- |
| Indoor: ☐ Furnace ☐ Air handler |  |  |  |  |
| Outdoor: ☐ AC ☐ Heat pump |  |  |  |  |
| Filter(s) | Size(s): [e.g., 20x25x1] · MERV [ ] · Qty [ ] · ☐ Customer supplies ☐ Plan includes |  |  |  |
| Refrigerant | ☐ R-410A ☐ R-32 ☐ R-454B ☐ R-22 ☐ Other [ ] · Metering device: ☐ TXV/EEV ☐ Fixed orifice · Line set [ft] |  |  |  |
| Thermostat | Model [ ] · ☐ Battery replaced · ☐ Wi-Fi |  |  |  |

Fill the nameplate rows at the first visit and carry them forward. The serial ties this visit to a specific covered unit on the maintenance agreement. A second system at the same address gets its own checklist.

## Part A: Every visit

| ✓ | Task | Check and target | Result |
| --- | --- | --- | --- |
| ☐ | Talk to the customer | Comfort complaints, noises, smells, water, high bills, renovations since the last visit. | Notes: |
| ☐ | Filter | Correct size and direction, housing sealed, no air bypassing the filter. | ☐ Replaced ☐ Cleaned ☐ Left in |
| ☐ | Thermostat, every mode | Heat, cool, fan, emergency heat on heat pumps. Settings and schedule confirmed. Battery yearly. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Registers and accessible duct | Open and unblocked. No crushed flex, loose joints, torn insulation, moisture or growth. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Static pressure (TESP) | Total against the rated TESP on the data tag (many air handlers: 0.50 in. w.c.). Return side at or above 0.4 points to a dirty filter or a small return. | Ret [ ] Sup [ ] Total [ ] in. w.c. ☐ Within rating ☐ Over |
| ☐ | Line voltage and disconnect | Voltage against nameplate. Disconnect intact, correct fuse, nothing bypassed, grounded. | [V] ☐ OK ☐ Attn ☐ Fail |
| ☐ | Connections and wiring | Tighten low and high voltage. Replace heat-discolored terminals and damaged wire. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Contactors and relays | Pitting, arcing, burned contacts. Replace on heavy arcing. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Blower motor and wheel | Wheel tight and clean, free rotation. Amps against FLA. Oil bearings only if the manufacturer says so. | [A] vs FLA [A] ☐ Wheel clean ☐ Needs cleaning |
| ☐ | Condensate drain, trap, pan | Flush the line, clear the trap, check the pan and the secondary pan. Test the float switch. Pan tablets compatible with the coil metal. | ☐ Flushed ☐ Float tested ☐ OK ☐ Attn ☐ Fail |
| ☐ | Cabinet and clearances | Panels tight, no cabinet air leaks, service and combustion clearances kept. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Safeties and control board | Test pressure switch, limit, float. Board jumpers set for the application. No scorched or bulged parts. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Accessories | Humidifier pad and line, UV bulb, media or electronic air cleaner, ERV/HRV filters, zone dampers. | ☐ None ☐ Serviced ☐ Attn |

## Part B: Spring visit (cooling)

Run in cooling 15 to 20 minutes before taking readings, with the outdoor temperature inside the manufacturer's operating range. Read return air at the grille and supply air a few feet from the coil.

| ✓ | Task | Check and target | Result |
| --- | --- | --- | --- |
| ☐ | Evaporator (indoor) coil | Fins clean, straight, open. Oil at a joint means a leak: bubble-test. Line insulation intact. | ☐ Clean ☐ Cleaned today ☐ Needs cleaning (quote) |
| ☐ | Condenser (outdoor) coil | Top off, clean inside out with coil cleaner and water, straighten fins, clear the base pan. Two feet of clearance all round. | ☐ Cleaned ☐ Rinsed only ☐ Attn |
| ☐ | Condenser fan motor | Blade tight, no wobble, free rotation. Amps against nameplate. | [A] vs [A] ☐ OK ☐ Attn |
| ☐ | Compressor | Running amps against RLA. Note any hard-start kit. | [A] vs RLA [A] ☐ OK ☐ Attn |
| ☐ | Run capacitors, under load | Measured µF against rated. Most are rated plus or minus 6 percent; outside that, recommend replacement. No bulge, no leak. | Herm [ ]/[ ] µF · Fan [ ]/[ ] µF · Blower [ ]/[ ] µF |
| ☐ | Air temperature split (delta T) | Return minus supply, dry bulb. Typical 16 to 22 °F at 400 CFM per ton; lower with humid return air, higher on 350 CFM per ton setups. High split = low airflow, low split = low capacity. Read it with the refrigerant numbers, never alone. | Ret [°F] Sup [°F] Split [°F] |
| ☐ | Refrigerant performance | Fixed orifice: superheat against the manufacturer's chart (indoor wet bulb, outdoor dry bulb), usually 5 to 25 °F. TXV/EEV: subcooling against the nameplate target. Probes over hoses; every hose connection loses refrigerant. Section 608 required. | Suction [psi] [°F] SH [°F] target [°F] · Liquid [psi] [°F] SC [°F] target [°F] |
| ☐ | Lines and joints | Oil stains, rubbing, missing suction insulation, service caps on and tight. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Heat pumps: reversing valve and defrost | Switch to heat and back; valve shifts. Force a defrost. Outdoor drain ports open, unit raised above the snow line. | ☐ N/A ☐ OK ☐ Attn ☐ Fail |
| ☐ | Finish | Panels on, disconnect pushed back in, thermostat at the customer's setting, system confirmed running before leaving. | ☐ Verified running |

## Part C: Fall visit (heating, gas furnace)

Fire on high stage 15 to 20 minutes before measuring rise or flue gases. Wear a low-level personal CO monitor. On an unsafe condition, shut the unit down and tell the customer in writing.

| ✓ | Task | Check and target | Result |
| --- | --- | --- | --- |
| ☐ | Burners | Remove and clean. Rust, debris, uneven or lifting flames when the blower starts. | ☐ Cleaned ☐ OK ☐ Attn ☐ Fail |
| ☐ | Heat exchanger | Cracks, rust, bulges, water marks. Flame disturbance at blower start is a red flag. Confirm with combustion numbers, never by eye alone. | ☐ OK ☐ Attn ☐ Fail, shut down |
| ☐ | Igniter | Hot surface: no cracks or white spots, cold resistance per manufacturer. Spark: gap and insulator. | [Ω] ☐ OK ☐ Attn ☐ Fail |
| ☐ | Flame sensor | Clean with fine steel wool or an abrasive pad, wipe, reinstall. Microamps in series: 0.5 to 10 µA depending on the furnace, 2 to 6 common. Replace only for a cracked insulator or an open rod. | [µA] ☐ Cleaned ☐ Replaced |
| ☐ | Gas pressure | Inlet at the inlet tap (utility if low). Manifold against the rating plate; adjust the valve. Leak-check every joint you touched. | Inlet [ ] Manifold [ ] rated [ ] in. w.c. |
| ☐ | Inducer and pressure switch | Inducer runs clean, no bearing noise. Switch proves; hose and port clear. | [A] ☐ OK ☐ Attn ☐ Fail |
| ☐ | Combustion analysis | Flue CO air-free: target under 100 ppm, AHRI Guideline X threshold 200. O2 and stack temperature per manufacturer. Ambient, return and supply CO: 0 target, 9 ppm maximum. | CO af [ppm] O2 [%] Stack [°F] · Ambient [ppm] Supply [ppm] |
| ☐ | Temperature rise | Supply minus return on high fire, supply probe several feet from the furnace. Inside the rating-plate range (for example 45 to 75 °F), ideally mid-range. High rise = low airflow. | Ret [°F] Sup [°F] Rise [°F] · plate [ ] to [ ] |
| ☐ | Limits and safeties | High limit opens and resets. Rollout switches intact. Door switch works. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Venting and combustion air | Flue or PVC intact, sloped, supported; no rust streaks, condensate or blockage; terminations clear. Combustion air per manufacturer and code. No combustibles near the vent. | ☐ OK ☐ Attn ☐ Fail |
| ☐ | Condensing furnace drain | Trap cleaned, drain flowing, neutralizer media checked. | ☐ N/A ☐ OK ☐ Attn |
| ☐ | Heat pumps: heating mode | Charge by the heating chart. Auxiliary heat stages and amps. Defrost board test. Crankcase heater. | ☐ N/A ☐ OK ☐ Attn ☐ Fail |
| ☐ | Finish | Panels on, thermostat at the customer's setting, home CO alarm present and tested, system confirmed running before leaving. | ☐ Verified running ☐ CO alarm OK |

## Findings and recommendations

| Item | What I found (reading, photo #) | Recommended action | Price | Customer |
| --- | --- | --- | --- | --- |
|  |  |  |  | ☐ Approved ☐ Declined |
|  |  |  |  | ☐ Approved ☐ Declined |
|  |  |  |  | ☐ Approved ☐ Declined |

Work beyond the inspection needs the customer's approval before it is done. Member discount applied: [ ]%.

## Sign-off

System condition today: ☐ Good ☐ Fair (see findings) ☐ Unsafe, shut down, customer notified in writing.

This maintenance visit was completed on [Date]. For maintenance agreement members, this is visit [1] of [2] for the plan year ending [Date], on the unit(s) listed above. Next visit due [Month, Year].

| Technician signature · name · date | Customer signature · name · date |
| --- | --- |

Keep a copy with the customer's equipment record and log the completed visit against the agreement. Single-system versions (AC, furnace, heat pump, tune-up, inspection, commercial) and the free agreement tracking spreadsheet: usedeepsel.com/checklists.