## Material list
Material list
Filled-in example. Replace the values, keep the columns. Size basis says where each size came from: the manual table, the nameplate or the code section. Ext. cost, totals and the Status dropdown are live.
Job # | 2026-0917
Customer / address | Example: 3-ton split AC and 96% gas furnace changeout, 35 ft line run, condenser moved to a new pad
System type | Split AC + gas furnace
Tonnage / AHRI ref | 3 ton / write the AHRI certificate number here
Line run (ft) | 35
Nameplate MCA / MOP (condenser) | 24 / 40 (example values, read yours off the nameplate)
Prepared by / date needed
Group | Item | Size / spec | Size basis | Qty | Unit | Unit cost | Ext. cost | Supplier / part # | PO # | Status | Qty used | Qty returned | Notes
Equipment
Equipment | Condenser, 3 ton | e.g. Trane 4TTR6036 | Sales scope | 1 | ea |  |  |  |  | ordered |  |  | Confirm model matches the AHRI certificate
Equipment | Cased evaporator coil, AHRI-matched |  | AHRI certificate | 1 | ea |  |  |  |  | ordered
Equipment | Gas furnace, 80 MBH, 96% AFUE | e.g. Goodman GMVC96 | Sales scope | 1 | ea |  |  |  |  | ordered
Equipment | External filter rack | EFR02 (Goodman accessory) | GMVC96 spec sheet | 1 | ea |  |  |  |  | quoted
Equipment | Thermostat |  | Sales scope | 1 | ea |  |  |  |  | quoted
Line set and refrigerant
Line set and refrigerant | Copper line set, insulated vapor line | 3/8 x 7/8 x 50 ft | Trane 4TTR6 guide, line size table (036-049 = 7/8 vapor). 3/8 x 3/4 for 018-030, 3/8 x 1-1/8 for 060 | 1 | ea |  |  |  |  | staged |  |  | Wrong size is the classic supply-house trip
Line set and refrigerant | Line isolators / hangers | one per 8 ft of vapor line | Trane 4TTR6 guide: isolators every 8 ft | 5 | ea |  |  |  |  | staged
Line set and refrigerant | Liquid-line filter drier | as shipped, field-installed | Trane 4TTR6 guide | 1 | ea |  |  |  |  | staged
Line set and refrigerant | Trim charge, R-410A | 0.60 oz per ft of 3/8 liquid line beyond the 15 ft factory charge: 20 ft x 0.60 | Carrier 24ACC6 product data (check your brand's table) | 12 | oz |  |  |  |  | staged |  |  | Charge to the invoice
Line set and refrigerant | Dry nitrogen | purge while brazing, pressure test 150 psig, evacuate to 350 microns | Trane 4TTR6 guide | 1 | cyl |  |  |  |  | loaded
Line set and refrigerant | Brazing rod, flux |  | Truck stock | 1 | set |  |  |  |  | loaded
Venting and gas
Venting and gas | PVC vent pipe | 2 in, 30 ft, 4 elbows. Allowed length checked against the 80 MBH column | Goodman IOG-2009 vent table (each elbow takes ~5 ft off a 2 in run) | 30 | ft |  |  |  |  | staged |  |  | If the run is over the table, go to 3 in
Venting and gas | PVC elbows, 90 degree | 2 in | Goodman IOG-2009 vent table | 4 | ea |  |  |  |  | staged
Venting and gas | Concentric termination kit | CVENT-2 (or CVENT-3 with 3 in pipe) | GMVC96 spec sheet | 1 | ea |  |  |  |  | staged
Venting and gas | Gas: ground-joint union, drip leg, manual shutoff, flex | 1/2 in FPT at the furnace | Goodman IOG-2009 (installer supplies), GMVC96 spec | 1 | set |  |  |  |  | staged
Electrical
Electrical | Disconnect, within sight of condenser | 60 A non-fused | NEC 440.14 (St. Paul 2023 NEC checklist); Johnstone G35-618 | 1 | ea |  |  |  |  | staged
Electrical | Two-pole breaker | 40 A (up to nameplate MOP) | Nameplate MOP; IAEI worked example MCA 24 / MOP 40 | 1 | ea |  |  |  |  | staged |  |  | Electrician confirms
Electrical | Conductors, condenser circuit | #12 Cu (carries nameplate MCA 24) | Nameplate MCA; NEC 440.6(A) nameplate governs | 40 | ft |  |  |  |  | staged |  |  | Confirm with AHJ
Electrical | Liquidtight whip | fastened within 12 in of the disconnect | St. Paul 2023 NEC checklist | 1 | ea |  |  |  |  | staged
Electrical | Service receptacle, GFCI, weather-resistant | within 25 ft of the equipment | NEC 210.63(A) | 1 | ea |  |  |  |  | quoted |  |  | Confirm 210.8(F) status with AHJ
Electrical | Furnace branch circuit | own circuit | NEC 422.12 | 1 | ea |  |  |  |  | quoted
Controls
Controls | Thermostat wire | 18/5 (18/8 for a heat pump with aux heat), 250 ft spool | DiversiTech 620-18-8 | 1 | spool |  |  |  |  | loaded |  |  | Physically check how many stat wires are at the old stat before install day
Condensate
Condensate | PVC drain and fittings, trap | 3/4 in, sloped 1/8 in per ft | IRC M1411 | 20 | ft |  |  |  |  | staged
Condensate | Float switch on primary pan auxiliary outlet | UL 508 device, 3/4 in adapter | IRC M1411; RectorSeal SS2 | 1 | ea |  |  |  |  | staged
Condensate | Secondary drain pan (attic coil) |  | IRC M1411 | 1 | ea |  |  |  |  | quoted |  |  | Skip if the coil is in the basement
Condensate | Condensate pump with safety switch | e.g. Little Giant VCMA-20ULS, 80 GPH | No gravity drain | 1 | ea |  |  |  |  | quoted |  |  | Put it on the list even when you think there is a drain
Duct
Duct | Supply plenum / return transition | field-measured | Site measure | 1 | set |  |  |  |  | ordered
Duct | Flex duct straps | 1-1/2 in wide, every 4 ft, sag under 1/2 in per ft | ADC flexible duct standard | 10 | ea |  |  |  |  | loaded
Duct | UL 181B-FX foil tape |  | IRC M1601.4.1 | 2 | roll |  |  |  |  | loaded
Duct | UL 181B-M mastic |  | IRC M1601.4.1 | 1 | gal |  |  |  |  | loaded
Pad and mounting
Pad and mounting | Plastic condenser pad | 36 x 36 x 3 (at least 1 in larger than the unit on all sides) | Trane 4TTR6 guide; DiversiTech standard pads | 1 | ea |  |  |  |  | staged |  |  | The row the boss forgets
Consumables
Consumables | Screws, hanger strap, sealant, zip ties |  | Truck stock | 1 | lot |  |  |  |  | loaded |  |  | Qty used tells you when truck stock is subsidizing jobs
Permit
Permit | Mechanical and electrical permits |  | AHJ | 1 | ea |  |  |  |  | ordered
[6 empty] | Material total | 0
[6 empty] | Markup % | 35%
[6 empty] | Material sell | 0
Not on this list: labor, crane or lift rental, disposal, sales tax. Cost columns are internal, the customer sees the estimate, never this tab.

## Material list - RTU
Material list - RTU
Filled-in example for a rooftop replacement. The curb adapter and the crane are the two rows with lead times, give them their own Status. Conductors and breaker come from the submitted unit's nameplate.
Job # | 2026-0921
Customer / address | Example: 7.5-ton gas/electric packaged rooftop unit replacing a unit on an existing curb
System type | Packaged RTU, gas heat
Tonnage / schedule mark | 7.5 ton / RTU-2 on the M-sheet
Old curb opening (measured) | write the measured opening here, the adapter is built to it
Nameplate MCA / MOP (submitted unit) | e.g. 21 / 30 at 460/3 on an AAON RN-007, use the submitted unit's plate, not the schedule
Prepared by / date needed
Group | Item | Size / spec | Size basis | Qty | Unit | Unit cost | Ext. cost | Supplier / part # | PO # | Status | Qty used | Qty returned | Notes
Equipment
Equipment | Packaged RTU, 7.5 ton gas/electric | per schedule mark RTU-2, submitted model | M-sheet schedule + submittal | 1 | ea |  |  |  |  | ordered |  |  | Schedule MCA/MOCP is basis of design, nameplate rules
Equipment | Thermostat / controller |  | Sales scope | 1 | ea |  |  |  |  | quoted
Curb and rigging
Curb and rigging | Curb adapter (or new curb + gasket) | built to the old curb opening; Carrier 48FC ships 14 in and 24 in curbs with gasket | MicroMetl curb adapter note; Carrier 48FC install instructions | 1 | ea |  |  |  |  | ordered |  |  | Drill and measure the old curb, send the drawing to the adapter maker
Curb and rigging | Crane lift | sized to operating weight (a 7-ton AAON RN-007 is 1,506 lb on the Region 12 schedule) | Unit submittal weight | 1 | ea |  |  |  |  | quoted |  |  | Book after the adapter ship date is confirmed
Accessories
Accessories | Outdoor-air hood / economizer | per unit option list | Carrier 48FC install steps | 1 | ea |  |  |  |  | ordered
Accessories | Flue hood |  | Carrier 48FC install steps | 1 | ea |  |  |  |  | ordered
Condensate
Condensate | Drain, external trap, fittings | 3/4 in, trap at least 4 in deep, pitched 1 in per 10 ft | Carrier 48FC install instructions | 1 | set |  |  |  |  | staged
Electrical
Electrical | Disconnect | factory non-fused option or field-installed | Carrier 48FC options; NEC 440.14 | 1 | ea |  |  |  |  | staged
Electrical | Conductors and breaker | from the submitted unit's nameplate (e.g. MCA 21 / MOCP 30 at 460/3) | Nameplate; NEC 440.6(A) | 1 | circuit |  |  |  |  | quoted |  |  | Electrician confirms wire and breaker before ordering
Electrical | Convenience outlet | factory option or field-installed within 25 ft | Carrier 48FC options; NEC 210.63(A) | 1 | ea |  |  |  |  | quoted
Controls
Controls | Duct smoke detector | required where return airflow exceeds 2,000 CFM | IMC 606.2.1 (WAC 51-52-0606) | 1 | ea |  |  |  |  | quoted |  |  | Fire alarm tie-in is a separate trade
Controls | Thermostat wire | 18/8, 250 ft spool | DiversiTech 620-18-8 | 1 | spool |  |  |  |  | loaded
Gas
Gas | Gas connection: union, drip leg, shutoff, flex | size per unit | Unit install instructions | 1 | set |  |  |  |  | staged
Duct
Duct | Supply and return transitions to the adapter | field-measured | Site measure | 1 | set |  |  |  |  | ordered
Duct | UL 181B-FX tape, 181B-M mastic, sealant |  | IRC M1601.4.1 (or local) | 1 | lot |  |  |  |  | loaded
Consumables
Consumables | Screws, hanger strap, zip ties, gasket sealant |  | Truck stock | 1 | lot |  |  |  |  | loaded
Permit
Permit | Mechanical, electrical, crane permit if the street is closed |  | AHJ | 1 | ea |  |  |  |  | ordered
[6 empty] | Material total | 0
[6 empty] | Markup % | 35%
[6 empty] | Material sell | 0
Not on this list: labor, crane or lift rental, disposal, sales tax. Cost columns are internal, the customer sees the estimate, never this tab.

## Equipment list
Equipment list (what is installed at the site, one row per unit)
Copy from the nameplate at startup or the first maintenance visit. Three example rows, replace them. Age is a formula off the install date.
Site / customer | Unit tag | Display name | Location on site | Area served | Type | Brand | Model | Serial | Manufacture date (from serial) | Install date | Age (yrs) | Capacity | Efficiency (metric + value) | Refrigerant | Full charge (lb) | V / Ph | MCA / MOP | Filter size x qty | Belt size (or direct drive) | Thermostat / controls | Warranty registered (date) | Parts warranty ends | Compressor / HX warranty ends | Labor warranty ends | Agreement plan | Last service | Next due | Condition (1-5) | Notes | Nameplate photo link
Example: 2-system house, Anytown | AC-1 | Downstairs A/C | Side yard | 1st floor | Split AC | Carrier | 24ACC636 | 2519E12345 (example) | week 25, 2019 (Carrier: digits 1-2 week, 3-4 year) | 2019-07-10 | 7 | 3 ton | SEER 16 (pre-2023 M rating) | R-410A | 7.5 | 208-230 / 1 | 24 / 40 | 16x25x1 x 1 | direct drive | Wi-Fi stat, hallway | 2019-07-20 | 2029-07-10 | 2029-07-10 | 2020-07-10 | Silver | 2026-04-14 | 2026-10-14 | 4 | Example row, replace with your unit. Registered inside Carrier's 90-day window.
Example: 2-system house, Anytown | F-1 | Basement furnace | Basement | Whole house | Gas furnace | Goodman | GMVC960803BN | 1906123456 (example) | June 2019 (Goodman: digits 1-2 year, 3-4 month) | 2019-07-10 | 7 | 80 MBH in | AFUE 96 |  |  | 115 / 1 |  | 16x25x1 rack (EFR02) | direct drive | Same stat as AC-1 | 2019-07-20 | 2029-07-10 | Lifetime HX (registered) | 2020-07-10 | Silver | 2025-10-20 | 2026-10-14 | 4 | Example row. Goodman's 10-year parts needs registration within 60 days.
Example: school building | RTU-5 | AG STEM rooftop | Roof, east | AG STEM classrooms | Packaged RTU, gas/electric | AAON | RN-007 |  |  | 2024-06-01 | 2 | 7 ton, 1,540 CFM | IEER 14.4 / EER 12.0 | R-410A | 14 | 460 / 3 | 21 / 30 | 20x25x2 x 4 (example) | belt (size from unit) | BAS |  |  |  |  | Quarterly commercial | 2026-07-08 | 2026-10-08 | 5 | Capacity, electrical and area from the Region 12 M601 schedule. Charge over 15 lb means the EPA 2026 leak-repair rule applies.
Formulas:
Age (yrs) = IF([Install date]="","",DATEDIF([Install date],TODAY(),"y"))

## Equipment schedule
Mechanical equipment schedule (drawing-set format)
Columns from three public drawing sets (Region 12 M601 2023, San Luis Obispo 2019, Florida restaurant 2025) plus the VA Division 23 closeout columns. Schedule values are basis of design; the submitted unit's nameplate governs wire and breaker. Label the efficiency metric (SEER2, IEER, pre-2023 SEER).
Mark | Area served | Location | Type | Basis of design (mfr / model) | Required capacity (load calc) | Nominal tons | Supply CFM | Min OA CFM | ESP (in wc) | Fan HP / drive | Cooling total MBH | Cooling sensible MBH | Heat type | Heating input MBH | Heating output MBH | Efficiency (metric + value) | Refrigerant | V / Ph / Hz | MCA | MOCP | Operating weight (lb) | Dimensions (in) | Curb height (in) | Filter | Line sizes (liq / suct) | Remarks | Closeout: manufacturer | Closeout: model | Closeout: serial | Closeout: submittal # | Closeout: TAB / Cx ref
RTU-5 | AG STEM | Roof | Packaged RTU | AAON RN-007 |  | 7 | 1540 | 880 | 2 | 2 HP, VFD |  |  | Gas |  |  | IEER 14.4 / EER 12.0 | R-410A | 460 / 3 / 60 | 21 | 30 | 1506 | 134 x 79 x 44 | 18 |  |  | Region 12 M601, Dec 2023
HP-1 | Per plan | Grade | Split heat pump, outdoor | Trane 4TWA4048 |  | 4 |  |  |  |  | 47 |  | Heat pump |  | 41.5 | SEER 14.5 / HSPF 8.2 / EER 12.0 (pre-2023 M ratings) | R-410A | 208 / 3 / 60 | 18 | 30 | 265 |  |  |  | per manufacturer | SLO 2019 set; pairs with FC-1
FC-1 | Per plan | Mechanical room | Fan coil / air handler | Trane GAM5A0C48 |  | 4 | 1600 | 275 | 0.5 | 3/4 HP |  |  | Aux electric (kW per schedule) |  |  |  |  | 208-230 / 1 / 60 | 8 | 15 | 170 |  |  | 22 x 20 x 1 MERV 8 |  | SLO 2019 set; pairs with HP-1
EF-3 | Welding shop | Roof | Exhaust fan, belt drive | Loren Cook 270RX11B |  |  | 4000 |  | 2 | 5 HP, VFD, 1,276 RPM | [7 empty] | 460 / 3 / 60 | [7 empty] | Region 12 M601; sones per schedule
CU-8 / ACU-8 | Per plan | Grade / ducted indoor | Ductless split, outdoor + ducted indoor | LG ARUN053GSS4 / ARNU483BRZ4 |  | 4.4 |  |  |  |  | 48.1 |  | Heat pump |  | 46.1 | SEER 17.0 | R-410A | 208 / 1 / 60 | 33 | 50 | [5 empty] | Region 12 M601
RTU-1(E) | Dining | Roof | Packaged RTU, existing to remain | Carrier 50FC |  | 5 | 2000 | 400 |  |  |  |  | Electric |  |  | SEER2 (column on the 2025 set) |  | 208-230 / 1 / 60 | V.I.F. | V.I.F. | [5 empty] | Florida 2025 set: verify electrical in field prior to ordering and bid

## Notes and sources
Notes and sources
How the tabs connect
Tab 4 (schedule) is what the engineer specifies. Tab 1 or 2 (material list) is what the crew buys and loads to install it. Tab 3 (equipment list) is what ended up on site, copied from the nameplates at startup, and it is what a maintenance agreement is written against. Fill the closeout columns on tab 4 and it becomes tab 3.
Line set sizes by brand (size from the manual for the unit you install)
Trane 4TTR6, Installer's Guide 18-AC98D1-5-EN | 018-030: 3/8 liquid x 3/4 vapor. 036-049: 3/8 x 7/8. 060: 3/8 x 1-1/8. Isolators every 8 ft of vapor line. Pressure test 150 psig with dry nitrogen, evacuate to 350 microns and hold under 500. Pad at least 1 in larger than the unit on all sides. Factory charge covers 15 ft.
Goodman condensing units, IO-101H (2004) | 0-24 ft runs: 2-3.5 ton 3/8 x 3/4; 4-5 ton 3/8 x 7/8. Longer runs: the larger vapor size is required for full ratings.
Carrier 24ACC6 product data | Trim charge 0.60 oz per ft of 3/8 liquid line beyond the 15 ft factory charge. The per-foot figure changes with liquid line size and brand.
Condensing furnace venting (Goodman IOG-2009 table) | 2 in PVC maximums run from 145 ft down to 45 ft with one elbow depending on input; 3 in maximums 217-238 ft. Each extra elbow takes about 5 ft off a 2 in run and 7 ft off a 3 in run. Minimum 5 ft plus one elbow. 2-1/2 or 3 in pipe can be used in place of 2 in. Installer supplies the gas union, drip leg and shutoff. Prime the trap.
Electrical (nameplate first, then the AHJ) | MCA sizes the conductors, MOP/MOCP caps the breaker. NEC 440.6(A): the nameplate governs. 440.14: disconnect within sight. 210.63(A): receptacle within 25 ft. 422.12: furnace on its own circuit. Worked example (IAEI): MCA 24, MOP 40, #12 Cu on a 40 A breaker. Liquidtight fastened within 12 in of the disconnect (St. Paul 2023 NEC checklist).
Condensate | IRC M1411: slope at least 1/8 in per ft, auxiliary drain at least 3/4 in, water-level switch to UL 508. Rooftop (Carrier 48FC): trap at least 4 in deep, pitch 1 in per 10 ft.
Duct | ADC flex duct standard: straps 1-1/2 in wide, no more than 4 ft apart, sag under 1/2 in per ft. IRC M1601.4.1: UL 181B-FX tape, 181B-M mastic.
Rooftop extras | Curb adapter when the new footprint differs from the old curb (MicroMetl). Duct smoke detector where return airflow exceeds 2,000 CFM (IMC 606.2.1).
Manufacture date from the serial (building-center.org)
Carrier / Bryant | Since 1980: digits 1-2 week, 3-4 year.
Trane / American Standard | 2002-2009: character 1 year, 2-3 week. 2010 on: 1-2 year, 3-4 week.
Lennox | Since 1973: 1-2 plant, 3-4 year, character 5 (letter) month.
Goodman / Amana | Digits 1-2 year, 3-4 month.
Rheem / Ruud | Common style (W2910...): digits 2-3 week, 4-5 year.
Warranty and refrigerant rules worth a column | Carrier: register within 90 days for 10-year parts (or 5-year parts + 3-year labor on some lines). Goodman: register within 60 days for 10-year parts, 5 unregistered. EPA leak repair from Jan 1, 2026: HFC appliances at 15 lb charge or more, 10% leak-rate threshold for comfort cooling, records kept 3 years. New residential and light commercial systems: 700 GWP limit, manufacture/import date Jan 1, 2025; VRF Jan 1, 2027.
Efficiency metrics | 2023 DOE test procedure change (Appendix M to M1): SEER/EER/HSPF became SEER2/EER2/HSPF2. AHRI example: 15 SEER / 8.8 HSPF under M = 14.3 SEER2 / 7.5 HSPF2 under M1. Units 65,000 Btuh and up are rated in IEER; 2023 minimum for 65-135 MBH air-cooled with electric or no heat moved from 12.9 to 14.8 IEER. Label the metric in every efficiency cell.
Sources and the article | Full source list with links: usedeepsel.com/hvac-material-list-template. Free from Deepsel, no email asked. Every free checklist and template: usedeepsel.com/checklists.