Free checklist from Deepsel · usedeepsel.com/hvac-tune-up-checklist · Version: September 2026 · Tasks follow ANSI/ACCA 4 QM. Target ranges are field rules of thumb; the data plate and the manufacturer's instructions win when they differ.

# HVAC Tune-Up Checklist and Report Card

| Customer | [Name] · [Phone] | Date | [Date] |
| --- | --- | --- | --- |
| Service address | [Street, City, State ZIP] | Technician | [Name] |
| Visit type | ☐ Cooling tune-up (spring) ☐ Heating tune-up (fall) ☐ Both | Agreement | ☐ Member, plan: [Tier] ☐ Non-member |
| Outdoor unit | [Make] · [Model] · [Serial] | Refrigerant | ☐ R-410A ☐ R-32 ☐ R-454B ☐ R-22 ☐ Other: [ ] |
| Indoor unit | ☐ Gas furnace ☐ Air handler ☐ Heat pump · [Make] · [Model] · [Serial] | Filter size(s) | [e.g. 20x25x1] |
| Thermostat | [Make / model] · Batteries: ☐ Replaced ☐ Not needed | Time on site | Arrived [ : ] · Left [ : ] |

## The 21 points, by visit

Result: OK = inspected, within spec or clean. Attn = out of spec, dirty, or a recommendation on page 2. N/A = not on this system. A point only counts when it was done; leave the box empty rather than ticking it.

| # | Cooling visit (spring) | OK / Attn / N/A | Heating visit (fall), gas furnace or heat pump | OK / Attn / N/A |
| --- | --- | --- | --- | --- |
| 1 | Thermostat: operation, calibration, level, batteries | ☐ ☐ ☐ | Thermostat: operation, calibration, heat call, batteries | ☐ ☐ ☐ |
| 2 | Air filter: inspect, replace, record size | ☐ ☐ ☐ | Air filter: inspect, replace, record size | ☐ ☐ ☐ |
| 3 | Indoor (evaporator) coil: inspect fins, clean if fouled | ☐ ☐ ☐ | Cabinet, clearances, combustibles near vent or furnace | ☐ ☐ ☐ |
| 4 | Condensate drain, pan, trap: flush, treat, test float switch | ☐ ☐ ☐ | Blower wheel cleanliness; blower motor amps vs nameplate FLA | ☐ ☐ ☐ |
| 5 | Blower wheel cleanliness; blower motor amps vs nameplate FLA | ☐ ☐ ☐ | Total external static pressure vs rated (typically 0.5" WC or less) | ☐ ☐ ☐ |
| 6 | Total external static pressure vs rated (typically 0.5" WC or less) | ☐ ☐ ☐ | Temperature rise across heat exchanger, inside nameplate range | ☐ ☐ ☐ |
| 7 | Temperature split, return to supply (about 16 to 22°F, humidity dependent) | ☐ ☐ ☐ | Heat exchanger: visual or camera inspection for cracks, rust, flame disturbance at blower start | ☐ ☐ ☐ |
| 8 | Refrigerant charge check: line temps, superheat (fixed orifice) or subcooling (TXV, about 8 to 14°F) | ☐ ☐ ☐ | Burners: inspect, clean, flame pattern steady and blue | ☐ ☐ ☐ |
| 9 | Refrigerant lines: insulation intact, no oil stains at joints | ☐ ☐ ☐ | Igniter: hot surface igniter cracks and ohms, or spark gap | ☐ ☐ ☐ |
| 10 | Outdoor (condenser) coil: wash, straighten fins, clear debris from base pan | ☐ ☐ ☐ | Flame sensor: clean, microamps recorded (1 to 10 µA, best 2 to 6) | ☐ ☐ ☐ |
| 11 | Condenser fan motor: amps vs FLA, blade balance, shaft endplay | ☐ ☐ ☐ | Inducer motor: amps, bearing noise, pressure switch hose and port | ☐ ☐ ☐ |
| 12 | Compressor amps vs nameplate RLA | ☐ ☐ ☐ | Gas pressure: inlet and manifold vs data plate (NG about 3.5" WC, LP about 10 to 11" WC) | ☐ ☐ ☐ |
| 13 | Run capacitor(s): microfarads under load vs rating, within 6% | ☐ ☐ ☐ | Combustion analysis: CO air-free under 100 ppm target; 400 ppm or more, shut down | ☐ ☐ ☐ |
| 14 | Contactor: pitting, burned contacts, coil, voltage drop | ☐ ☐ ☐ | Venting: slope, support, termination, rust, condensate, blockage | ☐ ☐ ☐ |
| 15 | Electrical connections: tightened, no heat discoloration, wire size matches load | ☐ ☐ ☐ | Combustion air supply correct for the appliance and the space | ☐ ☐ ☐ |
| 16 | Disconnect and fuse or breaker: correct size, not bypassed, case intact | ☐ ☐ ☐ | Safeties tested: high limit, rollout switches, pressure switch, door switch | ☐ ☐ ☐ |
| 17 | Line voltage measured vs nameplate | ☐ ☐ ☐ | Condensate trap and drain (condensing furnaces); outdoor drain ports (heat pumps) | ☐ ☐ ☐ |
| 18 | Control board and low voltage: 24 V present, no hot spots or burn marks | ☐ ☐ ☐ | Electrical: connections, disconnect, grounding, line voltage vs nameplate | ☐ ☐ ☐ |
| 19 | Cabinet, panels, clearance, pad level, unit free of debris and nests | ☐ ☐ ☐ | Control board and low voltage: 24 V present, no burn marks | ☐ ☐ ☐ |
| 20 | Visible ductwork: disconnected runs, leaks, crushed flex, missing insulation | ☐ ☐ ☐ | Heat pumps: reversing valve, defrost cycle, auxiliary heat strips and amps | ☐ ☐ ☐ |
| 21 | Final run test: full cooling cycle, disconnect back in, readings explained to customer | ☐ ☐ ☐ | Final run test: full heat call, ignition sequence, blower delays, ambient CO check, readings explained | ☐ ☐ ☐ |

Refrigerant is added only by an EPA Section 608 certified tech, and only after the leak is found. Record ounces and the leak-search result on page 2.

## Readings, before and after

Fill in every reading you took. A blank cell means the point was skipped, and that is fine to say. "After" only where you cleaned, adjusted or replaced something.

| Cooling reading | Target | Before | After |
| --- | --- | --- | --- |
| Outdoor / return air DB and WB, °F | Record conditions |  |  |
| Supply air dry bulb, °F | Record |  |  |
| Temperature split, °F | About 16 to 22; lower when the air is humid |  |  |
| Total external static pressure, " WC | Rated on data plate; 0.5 or less is typical |  |  |
| Suction line temperature / pressure | Record |  |  |
| Liquid line temperature / pressure | Record |  |  |
| Superheat or subcooling, °F | Chart or data plate value; 8 to 14 if none |  |  |
| Compressor amps / nameplate RLA | Under RLA |  |  |
| Condenser fan amps / nameplate FLA | Under FLA |  |  |
| Blower motor amps / nameplate FLA | Under FLA |  |  |
| Capacitor(s): rated µF / measured µF | Within 6% of rating |  |  |
| Line voltage, V | Nameplate range |  |  |
| Refrigerant added, oz (type) | Zero unless a leak was found and reported |  |  |

| Heating reading | Target | Before | After |
| --- | --- | --- | --- |
| Return / supply air temperature, °F | Supply read out of sight of the heat exchanger |  |  |
| Temperature rise, °F | Nameplate range, e.g. 45 to 75 |  |  |
| Total external static pressure, " WC | Rated on data plate; 0.5 or less is typical |  |  |
| Inlet / manifold gas pressure, " WC | Data plate; NG about 3.5, LP 10 to 11 |  |  |
| Flame sensor, µA | 1 to 10, best 2 to 6 |  |  |
| Flue CO air-free, ppm (and O2 %) | Under 100 and stable; 400 or more, shut down |  |  |
| Inducer motor amps / nameplate | Under nameplate |  |  |
| Blower motor amps / nameplate FLA | Under FLA |  |  |
| Ambient CO in living space, ppm | 0 · CO alarm present ☐ Yes ☐ No |  |  |

## Condition grades

A = within spec, no action. B = working, watch it, likely a recommendation next year. C = out of spec or unsafe, recommendation below. Grade what you measured.

| Component | Grade | Note | Component | Grade | Note |
| --- | --- | --- | --- | --- | --- |
| Compressor | ☐A ☐B ☐C |  | Heat exchanger | ☐A ☐B ☐C |  |
| Condenser fan motor | ☐A ☐B ☐C |  | Burners and igniter | ☐A ☐B ☐C |  |
| Blower motor and wheel | ☐A ☐B ☐C |  | Flame sensor | ☐A ☐B ☐C |  |
| Capacitor(s) | ☐A ☐B ☐C |  | Inducer motor | ☐A ☐B ☐C |  |
| Contactor | ☐A ☐B ☐C |  | Venting | ☐A ☐B ☐C |  |
| Indoor coil | ☐A ☐B ☐C |  | Gas piping and pressure | ☐A ☐B ☐C |  |
| Outdoor coil | ☐A ☐B ☐C |  | Safeties | ☐A ☐B ☐C |  |
| Condensate drain | ☐A ☐B ☐C |  | Ductwork (visible) | ☐A ☐B ☐C |  |
| Refrigerant circuit | ☐A ☐B ☐C |  | Thermostat and controls | ☐A ☐B ☐C |  |

## Recommendations

Every recommendation needs the reading that caused it. "Capacitor 40.1 µF on a 45 µF rating (11% low)" is a recommendation; "capacitor weak" is a guess. Photos attached: ☐ heat exchanger ☐ coils ☐ nameplates.

| Item | Reading vs spec (why) | Standard price | Member price | Decision |
| --- | --- | --- | --- | --- |
|  |  | $ | $ | ☐ Approved ☐ Declined |
|  |  | $ | $ | ☐ Approved ☐ Declined |
|  |  | $ | $ | ☐ Approved ☐ Declined |

| Status at departure | ☐ Running normally ☐ Shut down for safety, customer told in writing ☐ Disconnect reinstalled |
| --- | --- |
| Next visit due | [Season, month] · Visit [1 / 2] of [2] under the agreement year ending [Date] |
| Technician | [Signature] · [Printed name] · [Date] |
| Customer | I received a copy. Attn items and C grades were explained to me, with prices. [Signature] · [Date] |

One copy to the customer, one on file per unit; compare next year's readings against this sheet, the trend is the diagnosis. Not a substitute for the manufacturer's instructions, local code or safety training. Free from Deepsel, usedeepsel.com.