## Schedule
Customer / site | Unit | Equipment type | Frequency | Start month | Tech | Every (months) | Last done | Next due | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Due this month | Overdue | Notes
Anderson, Mark | Trane XR14 4TTR4036, closet | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Mike | 6 | 2026-04-02 | 2026-10-02 |  |  |  | 2026-04-02 | [5 empty] | Due |  |  |  | 0 | Gate code 4471
Baker, Janet | Goodman GSX140361, attic | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny | 6 | 2026-04-14 | 2026-10-14 |  |  |  | 2026-04-14 | [5 empty] | Due |  |  |  | 0
Castillo, Rosa | Carrier 24ACC636A003, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Mike | 6 | 2026-08-18 | 2027-02-18 |  |  | 2026-03-25 |  |  |  |  | 2026-08-18 | Due |  |  |  | Yes | 0 | Dog in yard, call first
Dawson, Phil | Rheem RA1436AJ1NA, closet | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny | 6 |  | 2026-04-01 |  |  |  | Due | [5 empty] | Due |  |  |  | 1 | Never booked spring
Ellis, Tanya | Lennox ML14XC1-036, attic | Split AC + gas furnace | Semiannual (spring + fall) | May | Mike | 6 | 2026-05-06 | 2026-11-06 |  |  |  |  | 2026-05-06 | [5 empty] | Due |  |  | 0
Foster, Greg | Trane XR13 4TTR3030, side yard | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny | 6 | 2026-04-21 | 2026-10-21 |  |  |  | 2026-04-21 | [5 empty] | Due |  |  |  | 0 | Renewal check not received
Garcia, Luis | Carrier 24VNA936A003, closet | Heat pump | Semiannual (spring + fall) | Jun | Mike | 6 |  | 2026-06-01 | [5 empty] | Due | [5 empty] | Due |  | 1 | Signed at June repair
Hughes, Dana | Goodman GSX160361, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-03-30 | 2026-09-30 |  |  | 2026-03-30 | [5 empty] | Due |  |  |  | Yes | 0 | Call before 9; fall booked 9/14
Ingram, Steve | Rheem RA1448AJ1NA, attic | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Mike | 6 | 2026-08-25 | 2027-02-25 |  |  |  | 2026-04-08 |  |  |  | 2026-08-25 |  | Due |  |  |  | 0
Jensen, Karen | Lennox XC21-036, closet | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny | 6 | 2026-04-30 | 2026-10-30 |  |  |  | 2026-04-30 | [5 empty] | Due |  |  |  | 0 | Prefers text; fall booked 9/22
Kowalski, Ben | Trane XR14 4TTR4030, side yard | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Mike | 6 | 2026-04-17 | 2026-10-17 |  |  |  | 2026-04-17 | [5 empty] | Due |  |  |  | 0
Lopez, Maria | Carrier 24ACC636A003, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-08-27 | 2027-02-27 |  |  | 2026-03-19 |  |  |  |  | 2026-08-27 | Due |  |  |  | Yes | 0
Mitchell, Ray | Goodman GSX140301, closet | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Mike | 6 | 2026-04-03 | 2026-10-03 |  |  |  | 2026-04-03 | [5 empty] | Due |  |  |  | 0 | Gate code 2210
Nguyen, An | Lennox ML14XC1-048, attic | Heat pump | Semiannual (spring + fall) | May | Danny | 6 | 2026-05-12 | 2026-11-12 |  |  |  |  | 2026-05-12 | [5 empty] | Due |  |  | 0
O'Brien, Kate | Rheem RA1636AJ1NA, closet | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Mike | 6 | 2026-04-27 | 2026-10-27 |  |  |  | 2026-04-27 | [5 empty] | Due |  |  |  | 0
Patel, Raj (unit 1) | Trane XV18 4TTV8036, downstairs | Heat pump | Semiannual (spring + fall) | Apr | Danny | 6 | 2026-08-20 | 2027-02-20 |  |  |  | 2026-04-24 |  |  |  | 2026-08-20 |  | Due |  |  |  | 0 | Downstairs
Patel, Raj (unit 2) | Trane XV18 4TTV8024, upstairs | Heat pump | Semiannual (spring + fall) | Apr | Danny | 6 | 2026-08-20 | 2027-02-20 |  |  |  | 2026-04-24 |  |  |  | 2026-08-20 |  | Due |  |  |  | 0 | Upstairs
Reyes, Carlos | Goodman GSX130361, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Mike | 6 | 2026-08-12 | 2027-02-12 |  |  | 2026-03-27 |  |  |  |  | 2026-08-12 | Due |  |  |  | Yes | 0
Sullivan, Pat | Carrier 24ABB336A003, side yard | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny | 6 |  | 2026-04-01 |  |  |  | Due | [5 empty] | Due |  |  |  | 1 | No answer x3
Thompson, Erin | Rheem RA1424AJ1NA, closet | Split AC + gas furnace | Semiannual (spring + fall) | May | Mike | 6 | 2026-05-29 | 2026-11-29 |  |  |  |  | 2026-05-29 | [5 empty] | Due |  |  | 0
Walsh, Tom | Lennox XC25-036, attic | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny | 6 | 2026-04-09 | 2026-10-09 |  |  |  | 2026-04-09 | [5 empty] | Due |  |  |  | 0 | Attic access, bring ladder; fall booked 9/8
Young, Brenda | Trane XR16 4TTR6036, garage | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Mike | 6 | 2026-08-14 | 2027-02-14 |  |  |  | 2026-04-28 |  |  |  | 2026-08-14 |  | Due |  |  |  | 0 | Lapsed, still to renew
Triangle Dental, Cary NC | Carrier 48TC 5-ton RTU-1, roof | Rooftop unit (RTU) | Quarterly | Jan | Mike | 3 | 2026-07-14 | 2026-10-14 | 2026-01-12 |  |  | 2026-04-09 |  |  | 2026-07-14 |  |  | Due |  |  |  | 0 | Filters 20x25x2 x2; roof hatch key at front desk
Cary Community Church | Lennox LGH 7.5-ton RTU-1, roof | Rooftop unit (RTU) | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-03-11 | 2026-09-11 |  |  | 2026-03-11 | [5 empty] | Due |  |  |  | Yes | 0 | Two units, same visit
Cary Community Church | Lennox LGH 7.5-ton RTU-2, roof | Rooftop unit (RTU) | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-03-11 | 2026-09-11 |  |  | 2026-03-11 | [5 empty] | Due |  |  |  | Yes | 0
Millbrook Dry Cleaners | Make-up air unit, back wall | Exhaust / make-up air | Monthly | Jan | Mike | 1 | 2026-08-04 | 2026-09-04 | 2026-01-06 | 2026-02-03 | 2026-03-03 | 2026-04-07 | 2026-05-05 | 2026-06-02 | 2026-07-07 | 2026-08-04 | Due | Due | Due | Due | Yes | 0 | Filter service only
Formulas:
Last done = IF(COUNT([Jan]:[Dec])=0,"",MAX([Jan]:[Dec]))
Next due = IF(OR([Every (months)]="",[Start month]=""),"",IF([Last done]="",DATE(YEAR(TODAY()),MATCH([Start month],J1:U1,0),1),EDATE([Last done],[Every (months)])))
Due this month = IF(COUNTIF([Jan]:[Dec],"Due")=0,"",IF(INDEX([Jan]:[Dec],1,MONTH(TODAY()))="Due","Yes",""))
Overdue = IF([Every (months)]="","",SUMPRODUCT(([Jan]:[Dec]="Due")*(COLUMN([Jan]:[Dec])-COLUMN([Jan])+1<MONTH(TODAY()))))

## Task list
Equipment | Task | How often | Best month(s) | Standard or source | Checklist page
Any forced-air system | Check the 1-inch filter; replace it when loaded | Check monthly; replace every 1 to 3 months | Every month | ENERGY STAR maintenance checklist | usedeepsel.com/hvac-maintenance-checklist
Any forced-air system | Replace 4 to 5 inch media filter | Every 6 to 12 months | Spring and fall visits | Filter manufacturer guidance | usedeepsel.com/hvac-maintenance-checklist
Air conditioner or heat pump (cooling) | Clean condenser coil; check refrigerant charge and temperature split; clear condensate drain; test capacitor and contactor; check blower amps | Annually | March to May | ENERGY STAR checklist; ACCA 4 Checklists 5.7 and 5.8 | usedeepsel.com/ac-maintenance-checklist
Gas furnace | Inspect heat exchanger, burners, flame sensor, gas pressure, venting; test safety controls | Annually | September to November | ENERGY STAR checklist; ACCA 4 Checklist 5.4 | usedeepsel.com/furnace-maintenance-checklist
Heat pump (heating) | Test defrost cycle, auxiliary heat and reversing valve | Annually | September to November | ACCA 4 Checklist 5.8-HP | usedeepsel.com/heat-pump-maintenance-checklist
Thermostat | Replace battery; check wiring and settings | Annually | Fall visit | ACCA 4 Checklist 5.3 | usedeepsel.com/hvac-inspection-checklist
UV lamp (if fitted) | Check lamp; replace per manufacturer (usually yearly) | Quarterly check | Each visit | ASHRAE/ACCA Standard 180 Table 5-2 | usedeepsel.com/hvac-maintenance-checklist
Condensate pump | Check and clean | Annually | Spring visit | ASHRAE/ACCA Standard 180 Table 5-7 | usedeepsel.com/ac-maintenance-checklist
Whole residential system | Full inspection with readings written down | Once per season of use (spring and fall) | March to May; September to November | ACCA 4 section 5.4 | usedeepsel.com/hvac-inspection-checklist
Rooftop unit | Filters; UV lamp | Quarterly | Jan, Apr, Jul, Oct | ASHRAE/ACCA Standard 180 Table 5-22 | usedeepsel.com/commercial-hvac-maintenance-checklist
Rooftop unit | Belt tension and sheaves; controls; P-trap; heat-exchange surface fouling; coil condition | Semiannually | Spring and fall | ASHRAE/ACCA Standard 180 Table 5-22 | usedeepsel.com/commercial-hvac-maintenance-checklist
Rooftop unit | Refrigerant temperatures; contactor; fan blades; drain pan growth; condenser surfaces; combustion section; dampers | Annually | Spring (cooling side), fall (heating side) | ASHRAE/ACCA Standard 180 Table 5-22 | usedeepsel.com/commercial-hvac-maintenance-checklist
Air handler | Filters; UV lamp | Quarterly | Jan, Apr, Jul, Oct | ASHRAE/ACCA Standard 180 Table 5-2 | usedeepsel.com/commercial-hvac-maintenance-checklist
Air handler | P-trap; VFD; controls | Semiannually | Spring and fall | ASHRAE/ACCA Standard 180 Table 5-2 | usedeepsel.com/commercial-hvac-maintenance-checklist
Condensing unit (commercial) | Controls; belts and sheaves; VFD | Semiannually | Spring and fall | ASHRAE/ACCA Standard 180 Table 5-8 | usedeepsel.com/commercial-hvac-maintenance-checklist
Condensing unit (commercial) | Refrigerant pressures; contactor; fan blades; coil fouling; condenser surfaces | Annually | Spring | ASHRAE/ACCA Standard 180 Table 5-8 | usedeepsel.com/commercial-hvac-maintenance-checklist
Exhaust, supply and return fans | Belt tension and wear | Semiannually | Spring and fall | ASHRAE/ACCA Standard 180 Table 5-14 | usedeepsel.com/commercial-hvac-maintenance-checklist
Exhaust, supply and return fans | Bearings; drive alignment; fan blades; dampers | Annually | Fall | ASHRAE/ACCA Standard 180 Table 5-14 | usedeepsel.com/commercial-hvac-maintenance-checklist
Air distribution | Clean grilles, registers and diffusers | Semiannually | Spring and fall | ASHRAE/ACCA Standard 180 Table 5-1 | usedeepsel.com/commercial-hvac-maintenance-checklist
Combustion furnace or unit heater (commercial) | Oil fuel filter monthly; air filters quarterly; heat exchanger, burner, flue and safeties annually | Monthly / quarterly / annually | Fall for the annual items | ASHRAE/ACCA Standard 180 Table 5-16 | usedeepsel.com/commercial-hvac-maintenance-checklist
Every unit | Write the visit and its readings into the equipment log | Every visit | Every visit | Your own records | usedeepsel.com/equipment-maintenance-log-template

## This month
Due in | September 2026 | [7 empty] | Still open from earlier months
Customer / site | Unit | Equipment type | Frequency | Start month | Tech | Every (months) | Last done | Next due | Customer / site | Unit | Equipment type | Frequency | Start month | Tech
Castillo, Rosa | Carrier 24ACC636A003, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Mike | 6 | 2026-08-18 | 2027-02-18 | Dawson, Phil | Rheem RA1436AJ1NA, closet | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny
Hughes, Dana | Goodman GSX160361, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-03-30 | 2026-09-30 | Garcia, Luis | Carrier 24VNA936A003, closet | Heat pump | Semiannual (spring + fall) | Jun | Mike
Lopez, Maria | Carrier 24ACC636A003, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-08-27 | 2027-02-27 | Sullivan, Pat | Carrier 24ABB336A003, side yard | Split AC + gas furnace | Semiannual (spring + fall) | Apr | Danny
Reyes, Carlos | Goodman GSX130361, garage | Split AC + gas furnace | Semiannual (spring + fall) | Mar | Mike | 6 | 2026-08-12 | 2027-02-12
Cary Community Church | Lennox LGH 7.5-ton RTU-1, roof | Rooftop unit (RTU) | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-03-11 | 2026-09-11
Cary Community Church | Lennox LGH 7.5-ton RTU-2, roof | Rooftop unit (RTU) | Semiannual (spring + fall) | Mar | Danny | 6 | 2026-03-11 | 2026-09-11
Millbrook Dry Cleaners | Make-up air unit, back wall | Exhaust / make-up air | Monthly | Jan | Mike | 1 | 2026-08-04 | 2026-09-04